## Cover Page
Nabukalu Community Tap stand Project, Bugiri
Blank BOQ Estimates

## Summary
Nabukalu Community Tap stand Project, Bugiri
GRAND SUMMARY
ITEM NO. | DESCRIPTION | AMOUNT (USHS.)
1 | BOREHOLE AND PUMP HOUSE | 0
2 | RESERVOIR/TANK | 0
3 | DISTRIBUTION | 0
4 | ELECTROMECHANICAL | 0
| SUB-TOTAL 1 | 0
| ADD 18% VAT | 0
| GRAND TOTAL | 0

## Borehole and Pump House
Nabukalu Community Tap stand Project, Bugiri
BILL NO. 1 BOREHOLE AND PUMP HOUSE
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
BOREHOLES AND PUMP HOUSE
Galvanised Mild Steel (GMS) pipes with threaded joints, all to BS 3601, not in trench and of the following sizes: (Transmission line and Wash out)
1.1.1 | 50 mm ND Transmision line | m | 14 |  | 0
1.1.2 | 40mm ND for Pump wash out | m | 6 |  | 0
1.1.3 | GMS double socketed long radius 90 degrees bends to BS 3601, flanges to ISO 2441 of 50mm ND | nr | 3 |  | 0
1.1.4 | GMS socketed bends 45 degrees 50mm ND | nr | 1 |  | 0
1.1.5 | All socketed gate valves to BS 5150 for operation by hand, to ND 50 mm | nr | 2 |  | 0
1.1.6 | Socketed GMS Non-Return Valves to ISO 2441 to PN 10 for ND 50 mm | nr | 1 |  | 0
1.1.7 | Socketed GMS Pressure Gauge N30 Series for ND 50 mm | nr | 1 |  | 0
1.1.8 | Socketed GMS Air valve for ND 50 mm | nr | 1 |  | 0
1.1.9 | GMS Tee 50x40mm for Pump Wash out | nr | 1 |  | 0
1.1.10 | Supply and install for well cover for the boreboles and all its accessories | nr | 1 |  | 0
BUILDING WORKS
1.1.11 | Construct a chain linked fence; 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 12.5 to BS 1722, with triple row of galvanised barbed wire gauge 10 on top, anchored into blockwork dwarf wall as per drawings, height 2.075m | M | 38 |  | 0
1.1.12 | Supply and fix gate to BS 3470, painted to Engineer's approval, of 2X2.075M as per attached drawing. Provide heavy duty pud lock for the gate | No. | 1 |  | 0
1.1.13 | Provide and lay machine crushed stone aggregate of size 25mm, at the entrance of the pump house done to specifications and satisifaction of the Engineer | m² | 2.47 |  | 0
1.1.14 | Plant paspalum grass in the compound of pump house/intake and provide watering during time of construction. See drawings | m² | 24.39 |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Reservoir
Nabukalu Community Tap stand Project
BILL NO.2 8000LITRES RESERVOIR/PLASTIC TANKS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
NB: It must be noted that the Pedestal of the well and its apron are already cast in place. Bidders should not include this in their cost.
2 | Element NO.1: Substructure
2.1 | Site Preparation
2.1.1 | Excavate over site to reduced levels commencing from stripped site level | m² | 36 |  | 0
2.1.2 | Dig out any existing termite mount, destory queen and apply approved anti-termite spray to the entire site | m² | 0 |  | 0
2.1.3 | Anti- termite treatment to sides and bottoms of foundation | m² | 28 |  | 0
2.1.4 | Ditto but stripped surfaces of the ground | m² | 7.84 |  | 0
2.1.5 | Ditto but blinded surface of hardcore | m² | 7.84 |  | 0
2.2 | Excavation and Earthworks |  |  |  | 0
2.2.1 | Excavate foundation trench not exceeding 1.5m deep commencing from reduced level | m³ | 16.8 |  | 0
2.2.2 | Ditto but column bases | m³ | 6 |  | 0
2.2.3 | Extra over excavations: breaking up rock met with in excavations | m³ | 2 |  | 0
2.3 | Disposal of excavated materials |  |  |  | 0
2.3.1 | Return, fill in and ram selected excavated material around the foundation around foundations and walling; placed in 200mm layers, watered and compacted to 95% MDD | m³ | 8.5 |  | 0
2.3.2 | Load, wheel and evenly spread out surplus soil on site | m³ | 8.3 |  | 0
2.4 | Fillings |  |  |  | 0
2.4.1 | 125mm murram filling: well watered and compacted to 95% MDD 95%: to make up levels under floor bed | m² | 6.6 |  | 0
2.4.2 | 150mm Hardcore bed: in broken stone well compacted, consolidated and blinded with and including 20mmlayer of lake/river sand well watered ready to receive concrete | m² | 6.6 |  | 0
2.4.3 | Ditto: Under splash aprons | m² | 3.996 |  | 0
2.5 | Concrete works |  |  |  | 0
2.5.1 | Mass concrete mix 1:4:8/38mm aggregate; 50mm thick blinding to foundations | m² | 23 |  | 0
2.5.2 | Mass concrete mix 1:3:6/20mm aggregate, in foundation trenches | m³ | 1.78 |  | 0
2.5.3 | Reinforced concrete in mix 1:1.5:3/20mm aggregate vibrated in |  |  |  | 0
2.5.4 | Column and Column Base | m³ | 0.8 |  | 0
2.5.5 | Reinforced concrete in mix 1:3:6/20mm aggregate vibrated in 100mm thick ground floor | m² | 9.18 |  | 0
2.6 | Sawn Form work |  |  |  | 0
2.6.1 | Ditto but Slab | m² | 9.18 |  | 0
2.7 | Reinforcement |  |  |  | 0
2.7.1 | Mild steel bar reinforcement to BS 4483 |  |  |  | 0
2.7.2 | Mesh A98 in floor slab weighing 1.58kg/m² | m² | 7.84 |  | 0
2.7.3 | 8mm bars(shear reinforcement to column) | Kg | 48 |  | 0
2.7.4 | 6mm bar as a chair/spacer for the column base | Kg | 1.5 |  | 0
2.7.5 | High yield tensile steel bar reinforcement to BS 4461 as described including cutting to lengths, bending, hoisting and fixing including all the ncessary binding wire and chair/ spacer blocks |  |  |  | 0
2.7.6 | 16mm bars | Kg | 170 |  | 0
2.8 | Sawn Form work |  |  |  | 0
2.8.1 | Ditto but Columns | m² | 12 |  | 0
2.9 | Foundation/Plinth Walls |  |  |  | 0
2.9.1 | Hard burnt clay bricks to BS 3921(3.5N/mm² compressive strength) bedded and jointed in cement and sand(1:3) mortar |  |  |  | 0
2.9.2 | 230mm wall | m² | 16.8 |  | 0
2.10 | Damp Proof Membrane |  |  |  | 0
2.10.1 | 1000 Gauge polythene sheet damp proof membrane in one layer with 300mm end laps: laid on blinded hardcore | m² | 6.6 |  | 0
2.10.2 | Horizontal Damp Proof Course(DPC) and Ant Proof Course(APC): hessian based bitumen felt: lapped 150mm on ends laid on cement and sand (1:3) mortar bed. APC average thickness of 25mm |  |  |  | 0
2.10.3 | 230mm wide: APC laid along the main layout of wall | m | 11.2 |  | 0
2.10.4 | DPC | roll | 2 |  | 0
2.11 | Plinth wall finishes |  |  |  | 0
2.11.1 | 15mm cement and sand(1:3) render: steel trowelled smooth | m² | 15.39 |  | 0
2.11.2 | Prepare and apply three coats bituminous or other approved water resistant paint to: rendered plinth wall | m² | 15.39 |  | 0
2.12 | Element NO.2: Building Frame |  |  |  | 0
2.12.1 | Reinforced in-situ concrete mix 1:1.5:3/20mm aggregate in |  |  |  | 0
2.12.2 | Columns | m³ | 1.5 |  | 0
2.12.3 | Ring beams | m³ | 1.9 |  | 0
2.12.4 | Slab but concrete mix 1:2:4/20mm aggregate | m³ | 1.67 |  | 0
2.12.5 | High yield tensile steel bar reinforcement to BS 4461 as described including cutting to lengths, bending, hoisting and fixing including all the ncessary binding wire and spacer blocks |  |  |  | 0
2.12.6 | 16mm bars for columns and ring beam | Kg | 367.9 |  | 0
2.12.7 | 8mm bars(shear reinforcement to column and beams) | Kg | 257.25 |  | 0
2.12.8 | 10mm bars for slabs | Kg | 74.55 |  | 0
2.13 | Sawn Form work to: |  |  |  | 0
2.13.1 | Sides and soffites: Beam | m² | 95.76 |  | 0
2.13.2 | Vertical sides: Column | m² | 88.32 |  | 0
2.13.3 | Soffites: Slab | m² | 9.18 |  | 0
2.14 | Element NO.3: Walls |  |  |  | 0
2.14.1 | Hard burnt clay bricks to BS 3921(3.5N/mm² compressive strength) bedded and jointed in cement and sand(1:3) mortar |  |  |  | 0
2.14.2 | 230mm Wall | m² | 17 |  | 0
2.14.3 | Square Hollow Section mild steel 60x60x3mm,primed with one coat of red oxide primer before fixing: complete with lugs built into wall, see drawings. Spacing of 200mm c/c including cutting and welding, | m | 36 |  | 0
2.14.4 | Concrete: Mass concrete of mix 1:2:4/20mm aggregate; 75mm cast on wall ready to receive SHS MS 60x60x3mm | m³ | 0.06 |  | 0
2.15 | Wall finishes |  |  |  | 0
2.15.1 | Internal Wall |  |  |  | 0
2.15.2 | Cement/lime putty/sand(1:2:9) |  |  |  | 0
2.15.3 | 15mm Plaster to wall: Walls and concrete surfaces: Steel trowelled smooth | m² | 17 |  | 0
2.15.4 | Prepare surfaces: apply three coats vinyl silk soft white emulsion paint: on steel trowelled plaster: to |  |  |  | 0
2.15.5 | Walls and concrete surfaces internally | m² | 17 |  | 0
2.15.6 | External Walls |  |  |  | 0
2.15.7 | 12mm cement and sand(1:4) wall rendering in two coats steel trowelled hard and smooth on wall externally | m² | 17 |  | 0
2.15.8 | Provide rough cast to external wall. See drawings; cement and sand (1:3) | m² | 17 |  | 0
2.15.9 | Prepare and apply three coats of plastic emulsion paint on rough cast walls externallly | m² | 17 |  | 0
2.15.10 | Ditto but on steel tube grills of 60x60x3mm SHS MS | m² | 62.5 |  | 0
2.15.11 | supply and fix on the wall inside the pump house a lockable cage measuring (1m x0.4m) as housing for the PV Disconnect and Charge Controller for the PV generator | Item | 1 |  | 0
2.16 | Floor Finishes |  |  |  | 0
2.16.1 | 25mm cement and sand (1:4) screed finished smooth | m² | 6.6 |  | 0
2.16.2 | 20x100 mm skirting with rounded top edge and coved at the jucntions with floor screed(mix of 1:3) | m | 10.28 |  | 0
2.16.3 | Prepare and apply three coats of gloss paint on skirting 100-200mm girth | m | 10.28 |  | 0
2.17 | Splash Apron |  |  |  | 0
2.17.1 | 75mm thick concrete of mix 1:3:6/25mm aggregate with all the necessary brick work and formwork. See drawings | m² | 4 |  | 0
2.18 | Door |  |  |  | 0
2.18.1 | Purpose made doors to the Enginer's Details. See detailed drawings. Primed with red oxide paint before delivery to site, painted blue on site complete with and including all the necessary hinges, metallic spikes, lugs and locking devices. Provide a heavy duty pud lock for the door. | Item | 1 |  | 0
2.19 | Solar Mounting Structure |  |  |  | 0
2.19.1 | Erect solar mounting structure, supply and install solar panels with all the accessories, access for cleaning the panels, lighting arrester, locking mechanism and pad locks for safety of the panels and other works associated with it as in the detailed drawings | Item | 1 |  | 0
2.20 | Water Tank and Plumbing System
2.20.1 | Supply and Install poly tanks of 8000litres plastic tank with a 1m wide access man way, ball float valve, fixed inlet (50mm diam), out let (40mm diam), overflow and washout (40mm) pipes connection complete with internal pipe work and fittings, bracings as detailed in the drawings | nr | 1 |  | 0
2.20.2 | Supply and fix iron sheet gauge 28 prepainted on the four vertical sides of the tank to protect the tank from sun radiation | m² | 29.84 |  | 0
2.20.3 | Supply and fix galvanised Mild Steel (GMS) pipes with threaded joints, all to BS 3601, not in trench and of the following sizes
2.20.4 | 40mm ND drop down pipe | M | 6 |  | 0
2.20.5 | GMS double socketed long radius 90 degrees bends to BS 3601, flanges to ISO 2441 of 40mm ND | nr. | 2 |  | 0
2.20.6 | All socketed gate valves to BS 5150 for operation by hand, to ND 40 mm | nr. | 1 |  | 0
2.20.7 | Socketed GMS Air valve for ND 40 mm | nr. | 1 |  | 0
2.20.8 | Socketed connecting Union/ connector 40mm | nr. | 2 |  | 0
2.20.9 | Socketed nipples 40mm | nr. | 2 |  | 0
2.20.10 | HDPE PN6 40mm OD male adapter | nr. | 1 |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Electro-Mechananical
Nabukalu Community Tapstand(CTS) Project
BILL NO.3 ELECTROMECHANICAL
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
ELECTRO-MECHANICAL WORKS
Submersible pump
3.1.1 | Lorentz pump as PS2-1800 HRE-32-2 Pumpset Q = 5.9m3/hr, H = 50m total head, with controller PS2-1800, Max. Power 1.8KW with a high efficiency EC Drive Brushless Motor; Model Lorentz Motor ECDRIVE 1800-HRE, Motor cable of 6mm2 See details in PV and Pump Sizing report attached | nr | 1 |  | 0
ELECTRICAL WORKS
Solar PV System
3.1.2 | LC310-P72, Polycrystalline Solar Panels, 930Wp, 8.25Imp, 37.5 Vmp See details in PV and Pump Sizing report | nr | 3 |  | 0
3.1.3 | PV Disconnect 440 - 40- 1 box connection with DC Disconnect Switch and Lightning surge protection with maximum voltage of 440V and maximum current of 40A, See details in PV and Pump Sizing report | nr | 1 |  | 0
3.1.4 | Surge protectors2, See details in PV and Pump Sizing report | nr | 1 |  | 0
0
3.1.5 | Well Probe V2, See details in PV and Pump Sizing report | nr | 1 |  | 0
0
3.1.6 | Assortment of electrical cables, interconnects and accessories for complete system wiring, including where necessary, underground cables, wired in fullconduit technique; supplied and installed to specifications. | sum | 1 |  | 0
0
0
Wiring and Riser Pipe Installation
3.1.7 | Motor cable (water resistent Cable), 6mm² | m | 50 |  | 0
0
3.1.8 | uPVC raiser pipe 50mm PN10 | nr | 8 |  | 0
0
3.1.9 | UPVC Adaptor set 50mm PN10 | set | 2 |  | 0
| Earthing and Lightening Protection |  |  |  | 0
3.1.10 | Complete with copper rod 16mm2 earth wire , copper wire, copper clamp, charcoal, damp salt for earthing . Ligtening complete with copper rod, copper tape , copper spike , copper bolt at the solar structure | nr | 1 |  | 0
Water Monitoring system
0
3.1.11 | Bulk Meter, WP Water meter DN50, See details in the PV & Pump Sizing report attached | nr | 1 |  | 0
| Carried to Summary |  |  |  | 0
| Page 1 |  |  |  | 0
TOTAL TO GRAND SUMMARY

## Distribution main
Nabukalu Community Tapstands Project
BILL NO.4 DISTRIBUTION SYSTEM
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
DEMOLITION & SITE CLEARANCE
4.1.1 | General clearance along pipeline | m | 620 |  | 0
| PLASTIC PRESSURE PIPES |  |  |  | 0
| HDPE pipes to BS 5114 or its equivalent and in trench depth not exceeding 1.5 m. |  |  |  | 0
| PN6 |  |  |  | 0
4.1.2 | OD 40mm | m | 500 |  | 0
4.1.3 | OD32mm | m | 200 |  | 0
PIPEWORK-FITTINGS AND VALVES
HDPE Tee
Equal Tee - PN6
4.1.4 | 40X40mm OD | No. | 1 |  | 0
Reducing Tee - PN6
4.1.5 | 40x32 mm OD | No. | 3 |  | 0
Reducing Connector - PN6
4.1.6 | 40X32mm OD | No. | 3 |  | 0
0
| PE Coupling |  |  |  | 0
4.1.7 | 40mm OD | No. | 3 |  | 0
4.1.8 | 32mm OD | No. | 3 |  | 0
| Collection 1 to Summary |  |  |  | 0
4.1.9 | Marker posts for pipelines as per drawings. | No. | 4 |  | 0
0
0
4.1.10 | Construct a double faucet Stand Post complete as in the detailed drawing including all earthwork, building work, concrete works, plumbing, drains and soak pit, all relevant fitings; galvanized iron pipe and fittings, brass stop cock, lockable steel meter protection box, taps and domestic water meter, raising meter above ground, GI/HDPE connection, all to PN6 | No. | 3 |  | 0
| Collection 2 to Summary |  |  |  | 0
| Page 1: Collection 1 to Summary |  |  |  | 0
| Page 2: Collection 2 to Summary |  |  |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0