## Summary
# | Item description | Purchase request reference number. |  | Quantity of requirement
|  |  | Unit | In Pcs
1 | Diesel generator sets of 50KVA, which is water cooled and open type, with all the required accessories. (Air cleaner, oil filter etc) | ADD-BPH-5208 | SET | 1
2 | Diesel generator sets of 60KVA, which is water cooled and open type, with all the required accessories, (air cleaner, oil filter etc) | ADD-BPH-5208 | SET | 1
3 | Diesel generator sets of 30KVA, which is water cooled and open type, with all the required accessories (air cleaner, oil filter etc) | ADD-BPH-5208 | SET | 1
4 | Submersible pump having a capacity of (18.5KW), with 18.5KW control panel board (switch board), star (y) connection/starting system or auto TRF connection type, discharge 7 lit/sec, pump diameter less than or equal to 6", head- 353m, rewindable and made of stainless steel. With accessories as given in the specification | ADD-BPH-5208 | SET | 1
5 | Submersible pump having a capacity of (45 KW), with 45 KW control panel board (switch board), star (y) connection/starting system or auto TRF connection type, discharge 5 lit/sec, pump diameter less than or equal to 6", head- 230 m, rewindable and made of Set 1 1391304.35 1391304.35 stainless steel. With accessories as given in the specification | ADD-BPH-5208 | SET | 1
6 | 18.5KW control panel board (switch board), star (y) connection/starting system and auto TRF connection type | ADD-BPH-5208 | SET | 1
7 | 13 KW control panel board (switch board), star (y) connection/starting system and auto TRF connection type | ADD-BPH-5208 | set | 1
8 | Supply 30 KW HotWater Submersible Pump Set. | AFA-BPH-6972 | set | 1
9 | Supply of 75 KVA Star-delta Starting Generator, which is water cooled and open type, with all the required accessories (air cleaner, oil filter etc) | AFA-BPH-6972 | set | 1
10 | Supply 30 KW Switch board for submersible pump | AFA-BPH-6972 | set | 1
11 | Supply of 30 KVA Star-delta Starting Generator, which is water cooled and open type, with all the required accessories, (air cleaner, oil filter etc) | AFA-BPH-6972 | set | 1
12 | Supply of 11 KW Hot Water Submersible Pump Set | AFA-BPH-6972 | set | 1
13 | Supply 11 KW Switch board for submersible pump | AFA-BPH-6972 | set | 1

## 1. Spec 50KVA Generator
Spec 50 KVA Generator
Generator specification for for 04 Laste Gerado Kebele, Gubalafto woreda, North Wollo Zone, Amhara Region
System
Engine | Fuel system | Diesel
12 volt fail safe actuator
In-line direct injection/Rotray pump
Fuel pump injection system with integral Electronic governor
Spin-on paper element fuel filters
Standard fuel water separator.
| Engine Stroke: | 4 cycle
| PRP (primer running power) | 50 kVA/40 kW
| ESP (emergency stand by power) | 60kVA/48 kW
| speed | 1500rpm
| Aspiration | Turbocharged
| Starting System | Electric
| Filters | Air cleaner with dry element and restriction indicator
Spin full flow lube oil filter
Oil cooler Drin tap
Drain Tap
| cooling system | Water
Alternator | Rating out put | 40KW
| Power out put | 50Kva
| Phase | Three Phase
| Frequency | 50
| Power factor | cos ϕ 0.8
| Poles | 4
| Type | Open type, Brushless, self exciting
| Insulation | Class (H)
| With fan cooling | Yes
| Self regulating | Yes
| Frame Base | Anti-vibration mountings properly sized
Welded or Screwed support legs
| PROTECTIONS WITH SHUTDOWN | Low fuel level
Battery charger failure
low oil pressure
high engine temperature
Circuit breaker protection
Emergency stop button
| External interface | 3P+N+T 400V
230V
| Display (volts, Amps and Hour meter) | Digital or analog multi

## 2. Spec 60KVA Generator
Spec 60 KVA Generator
Generator specification for 09 Keyu Gariya Kebele, Raya Kobo Woreda, North Wollo Zone Amhara Region
System
Engine | Fuel system | Diesel
12 volt fail safe actuator
In-line direct injection/Rotray pump
Fuel pump injection system with integral Electronic governor
Spin-on paper element fuel filters
Standard fuel water separator.
| Engine Stroke: | 4 cycle
| PRP (primer running power) | 60 kVA/48 kW
| ESP (emergency stand by power) | 70kVA/56 kW
| speed | 1500rpm
| Aspiration | Turbocharged
| Starting System | Electric
| Filters | Air cleaner with dry element and restriction indicator
Spin full flow lube oil filter
Oil cooler Drin tap
Drain Tap
| cooling system | Water
Alternator | Rating out put | 48KW
| Power out put | 60KVA
| Phase | Three Phase
| Frequency | 50
| Power factor | cos ϕ 0.8
| Poles | 4
| Type | Open type, Brushless, self exciting
| Insulation | Class (H)
| With fan cooling | Yes
| Self regulating | Yes
| Frame Base | Anti-vibration mountings properly sized
Welded or Screwed support legs
| PROTECTIONS WITH SHUTDOWN | Low fuel level
Battery charger failure
low oil pressure
high engine temperature
Circuit breaker protection
Emergency stop button
| External interface | 3P+N+T 400V
230V
| Display (volts, Amps and Hour meter) | Digital or analog multi
| Ambient temperature | Greater than or equal to 40 degree Celsius

## 3. Spec 30KVA Generator
Spec 30 KVA Generator
Generator specification for 014 Gedida Kebele, Worebabo Woreda, South Wollo Zone, Amhara Region
System
Engine | Fuel system | Diesel
12 volt fail safe actuator
In-line direct injection/Rotray pump
Fuel pump injection system with integral Electronic governor
Spin-on paper element fuel filters
Standard fuel water separator.
| Engine Stroke: | 4 cycle
| PRP (primer running power) | 30 kVA/24 kW
| ESP (emergency stand by power) | 33 kVA/26.4 kW
| speed | 1500rpm
| Aspiration | Turbocharged
| Starting System | Electric
| Filters | Air cleaner with dry element and restriction indicator
Spin full flow lube oil filter
Oil cooler Drin tap
Drain Tap
| cooling system | Water
Alternator | Rating out put | 24 KW
| Power out put | 30 Kva
| Phase | Three Phase
| Frequency | 50
| Power factor | cos ϕ 0.8
| Poles | 4
| Type | Open type, Brushless, self exciting
| Insulation | Class (H)
| With fan cooling | Yes
| Self regulating | Yes
| Frame Base | Anti-vibration mountings properly sized
Welded or Screwed support legs
| PROTECTIONS WITH SHUTDOWN | Low fuel level
Battery charger failure
low oil pressure
high engine temperature
Circuit breaker protection
Emergency stop button
| External interface | 3P+N+T 400V
230V
| Display (volts, Amps and Hour meter) | Digital or analog multi

## 4.Spec Submersible pump 18.5 KW
TECHNICAL SPECIFICATIONS FOR 18.5 SUBMERSIBLE PUMP
I. Submersible pump for 04 Laste Gerado Kebele, Gubalafto woreda, North Wollo Zone, Amhara Region
For the 18.5 KW submersible pump the discharge is 4 l/s and Head 353 meter
S/No | Details of Technical specifcations | Remarks
1 | The Submersible pump need to have the following specifications
1.1 | The submersible pump is made of stainless steel , have unique and patented floating impellers to give clearance to make easier the water to flow in to the pump with important hydraulic and functional advantages | 1 Pcs
High efficiency
Resistive to sand( Erosion almost totally eliminated)
Longer working duration
Minimum hydraulic maintenance
The structure of the pump is compact ,short,robust and absolute relibality even in wells with significant quantities of sand containing and chemically aggressive
Water level control
Star and delta contactors
Rewindable
Technical operating / Performance data
Flow (Dischrage lit/sec)- 4 lit/sec
Head (M)- 353m
Efficency- 66%
Power - 18.5KW
Pump diameter- ≤ 6 "
Pump outlet size- 2"
1.2 | Control panel and other components | 1 Pcs
18.5 KW control panel board (switch board), star (y) connection/starting system or auto TRF connection type and with all the required accessories
| Flexible PVC insulated cable (Four phase) , size 3*25mm2 | 200m
| Flexible PVC insulated electrode sensor cable , size 1*1.5mm2 | 200m
| Electrode sensor | 1 pcs
| Volcanization kit ,GT2 | 1 pair
| Cable clamp | 1 pkt
| Pipe clamp (2") | 2 pairs
| Class "C" 2" GS (Red marked) riser pipes ,having 6m length each | 20 Pcs

## 5.Spec Submersible pump 45 KW
TECHNICAL SPECIFICATIONS FOR 45 KW SUBMERSIBLE PUMP
I. Submersible pump for 018 Kalim Kebele, Raya Kobo woreda, North Wollo Zone, Amhara Region
For the 45 KW submersible pump the discharge is 15 l/s and head 230 meter (The Borehole casing is 8 inch)
S/No | Details of Technical specifcations | Remarks
1 | The Submersible pump need to have the following specifications
1.1 | The submersible pump is made of stainless steel , have unique and patented floating impellers to give clearance to make easier the water to flow in to the pump with important hydraulic and functional advantages | 1 Pcs
High efficiency
Resistive to sand( Erosion almost totally eliminated)
Longer working duration
Minimum hydraulic maintenance
The structure of the pump is compact ,short,robust and absolute relibality even in wells with significant quantities of sand containing and chemically aggressive
Water level control
Star and delta contactors
Rewindable
Technical operating / Performance data
Flow (Dischrage lit/sec)- 12-15 lit/sec
Head (M)- 230 m
Efficency- 66%
Power - 45 KW
Pump diameter- ≤ 8 "
Pump outlet size- 4"
1.2 | Control panel and other components | 1 Pcs
45 KW control panel board (switch board), star (y) connection/starting system or auto TRF connection type and with all the required accessories
| Flexible PVC insulated cable (Four phase) , size 3*25mm2 | 150m
| Flexible PVC insulated electrode sensor cable , size 1*1.5mm2 | 150m
| Electrode sensor | 1 pcs
| Volcanization kit ,GT2 | 1 pair
| Cable clamp | 1 pkt
| Pipe clamp (2") | 2 pairs
| Class "C" 4" GS (Red marked) riser pipes ,having 6m length each | 17 Pcs

## 6. Spec for Swich Board 18.5 KW
Spec for Switch Board
I. Switch board for Amhara Region, North Wollo Zone, Raya Kobo woreda , 09 Kayu Gariya Kebele
S/No | Details of Technical specifcations | Remarks
1.1 | Control panel and other components | 1 Pcs | Price
18.5KW control panel board (switch board), star (y) connection/starting system and auto TRF connection type and with all the required accessories

## 7. Spec for Swich Board 13 KW
Spec for Switch Board
1 Switch board for Amhara Region, South Wollo Zone, Worebabo woreda , 014 Gedida Kebele
S/No | Details of Technical specifcations | Remarks
2.1 | Control panel and other components | 1 Pcs | Price
| 13 KW control panel board (switch board), star (y) connection/starting system and auto TRF connection type and with all the required accessories |  | 200000

## 8. Spec Hot Water SP 30 KW
TECHNICAL SPECIFICATIONS FOR 30 KW HOT WATER SUBMERSIBLE PUMP
I. Submersible pump for Elidar Woreda,Zone 1, Afar Region
S/No | Details of Technical specifcations | Remarks
1 | The Submersible pump need to have the following specifications
1.1 | The submersible pump is made of stainless steel , have unique and patented floating impellers to give clearance to make easier the water to flow in to the pump with important hydraulic and functional advantages | 1 Pcs
High efficiency
Resistive to sand( Erosion almost totally eliminated)
Longer working duration
Minimum hydraulic maintenance
The structure of the pump is compact ,short,robust and absolute relibality even in wells with significant quantities of sand containing and chemically aggressive
Water level control
Star and delta contactors
Rewindable
Technical operating / Performance data
Flow (Dischrage lit/sec)- 7 lit/sec
Head (M)- 353m
Efficency- 66%
Power - 30 KW
Pump diameter- ≤ 6 "
Pump outlet size- 2"
1.2 | Control panel and other components | 1 Pcs
30 KW control panel board (switch board), star (y) connection/starting system and auto TRF connection type and with all the required accessories
| Flexible PVC insulated cable (Four phase) , size 3*25mm2 | 200m
| Flexible PVC insulated electrode sensor cable , size 1*1.5mm2 | 200m
| Electrode sensor | 1 pcs
| Volcanization kit ,GT2 | 1 pair
| Cable clamp | 1 pkt
| Pipe clamp (2") | 2 pairs
| Class "C" 2" GS (Red marked) riser pipes ,having 6m length each | 20 Pcs

## 9. Spec 75 KVA Generator
Spec 75 KVA Generator
Generator specification for Zone 1(Awsi Rasu), Elidar Woreda, Su’da Kebele , Afar Region
System
Engine | Fuel system | Diesel
12 volt fail safe actuator
In-line direct injection/Rotray pump
Fuel pump injection system with integral Electronic governor
Spin-on paper element fuel filters
Standard fuel water separator.
| Engine Stroke: | 4 cycle
| PRP (primer running power) | 75 kVA/48 kW
| ESP (emergency stand by power) | 80kVA/56 kW
| speed | 1500rpm
| Aspiration | Turbocharged
| Starting System | Electric
| Filters | Air cleaner with dry element and restriction indicator
Spin full flow lube oil filter
Oil cooler Drin tap
Drain Tap
| cooling system | Water
Alternator | Rating out put | 48KW
| Power out put | 75 KVA
| Phase | Three Phase
| Frequency | 50
| Power factor | cos ϕ 0.8
| Poles | 4
| Type | Open type, Brushless, self exciting
| Insulation | Class (H)
| With fan cooling | Yes
| Self regulating | Yes
| Frame Base | Anti-vibration mountings properly sized
Welded or Screwed support legs
| PROTECTIONS WITH SHUTDOWN | Low fuel level
Battery charger failure
low oil pressure
high engine temperature
Circuit breaker protection
Emergency stop button
| External interface | 3P+N+T 400V
230V
| Display (volts, Amps and Hour meter) | Digital or analog multi
| Ambient temperature | Greater than or equal to 40 degree Celsius

## 10.Spec for Swich Board 30 KW
Spec for Switch Board
I. Switch board for Afar Region, Zone1, Elidar Woreda
S/No | Details of Technical specifcations | Remarks
1.1 | Control panel and other components | 1 Pcs | Price
30 KW control panel board (switch board), star (y) connection/starting system and auto TRF connection type and with all the required accessories

## 11. Spec 30KVA Generator
Spec 30 KVA Generator
Generator specification for Zone2, (Kilbeti Rasu) Berhale Woreda, Adda Kebele Region
Engine | Fuel system | Diesel
12 volt fail safe actuator
In-line direct injection/Rotray pump
Fuel pump injection system with integral Electronic governor
Spin-on paper element fuel filters
Standard fuel water separator.
| Engine Stroke: | 4 cycle
| PRP (primer running power) | 30 kVA/24 kW
| ESP (emergency stand by power) | 33 kVA/26.4 kW
| speed | 1500rpm
| Aspiration | Turbocharged
| Starting System | Electric
| Filters | Air cleaner with dry element and restriction indicator
Spin full flow lube oil filter
Oil cooler Drin tap
Drain Tap
| cooling system | Water
Alternator | Rating out put | 24 KW
| Power out put | 30 Kva
| Phase | Three Phase
| Frequency | 50
| Power factor | cos ϕ 0.8
| Poles | 4
| Type | Open type, Brushless, self exciting
| Insulation | Class (H)
| With fan cooling | Yes
| Self regulating | Yes
| Frame Base | Anti-vibration mountings properly sized
Welded or Screwed support legs
| PROTECTIONS WITH SHUTDOWN | Low fuel level
Battery charger failure
low oil pressure
high engine temperature
Circuit breaker protection
Emergency stop button
| External interface | 3P+N+T 400V
230V
| Display (volts, Amps and Hour meter) | Digital or analog multi

## 12. Spec Hot Water SP 11 KW
TECHNICAL SPECIFICATIONS FOR 11 KW HOT WATER SUBMERSIBLE PUMP
Submersible pump for Berhale Woreda Zone 2, Afar Region
S/No | Details of Technical specifcations | Remarks
1 | The Submersible pump need to have the following specifications
1.1 | The submersible pump is made of stainless steel , have unique and patented floating impellers to give clearance to make easier the water to flow in to the pump with important hydraulic and functional advantages | 1 Pcs
High efficiency
Resistive to sand( Erosion almost totally eliminated)
Longer working duration
Minimum hydraulic maintenance
The structure of the pump is compact ,short,robust and absolute relibality even in wells with significant quantities of sand containing and chemically aggressive
Water level control
Star and delta contactors
Rewindable
Technical operating / Performance data
Flow (Dischrage lit/sec)- 5 lit/sec
Head (M)- 180 m
Efficency- 66%
Power - 11 KW
Pump diameter- ≤ 6 "
Pump outlet size- 2"
1.2 | Control panel and other components | 1 Pcs
11 KW control panel board (switch board), star (y) connection/starting system and auto TRF connection type and with all the required accessories
| Flexible PVC insulated cable (Four phase) , size 3*25mm2 | 150m
| Flexible PVC insulated electrode sensor cable , size 1*1.5mm2 | 150m
| Electrode sensor | 1 pcs
| Volcanization kit ,GT2 | 1 pair
| Cable clamp | 1 pkt
| Pipe clamp (2") | 2 pairs
| Class "C" 2" GS (Red marked) riser pipes ,having 6m length each | 17 Pcs

## 13. Spec for Swich Board 11 KW
Spec for Switch Board
1. Switch board for Afar Region, Zone2, Berhale Woreda
S/No | Details of Technical specifcations | Remarks
2.1 | Control panel and other components | 1 Pcs | Price
11 KW control panel board (switch board), star (y) connection/starting system and auto TRF connection type and with all the required accessories