## Cover
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BIDDER'S ESTIMATE - Lot 1
Bidder's Estimate for Muwayo TC -piped water supply scheme

## Preamble
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BIDDER'S ESTIMATE - Lot 1
Preamble: This BoQ relates to the proposed construction of the mini-piped water scheme at Muwayo TC. The BoQ should be read together with the drawings and the technical specifications. The project consists of a pumping station, the transmission pipeline, storage tanks and distribution pipelines. Water is pumped from a borehole of yield 14.4m3/hour yield using solar powered pump. The water is pumped to a reservoir approx 2.4km from the borehole to a reservoir of 75m3 , elevated 1.5m on a pedestal. The project has allowed for 15 PSP for water collection.
Lot 1 scope: This covers works at the reservior station including the installation of a 75m3 reservior on an elevated 1.5m pedestal, and all associated installations and civil works and as described in the BoQ.

## Grand Summary
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BIDDER'S ESTIMATE - Lot 1
GRAND SUMMARY
Bill No | Bill Description | INVESTMENT COST
GENERAL
M-G-1 | GENERAL ITEMS | 0
M-G-2 | METHOD RELATED CHARGES | 0
M-G-3 | DAYWORKS
| SUB-TOTAL | 0
WATER SUPPLY AND EQUIPMENT
MUWAYO WATER SUPPLY NETWORK
M-W-1 | MUWAYO BOREHOLE PUMP STATION DEVELOPMENT | 0
M-W-2 | MUWAYO PUMP AND GUARD HOUSE | 0
M-W-3 | MUWAYO PUMPING MAINS | 0
M- W-4 | STORAGE RESERVOIR TANK | 0
M-W-5 | STORAGE RESERVOIR SITE WORKS | 0
M- W-6 | MUWAYO DISTRIBUTION NETWORK | 0
M-W-7 | INTENSIFICATION NETWORKS
M-W-8 | CONSUMER CONNECTIONS | 0
M-W-9 | MECHANICAL & ELECTRICAL WORKS | 0
GENERAL CONSTRUCTION WORKS
M-W-10 | GUARD AND PUMP ATTENDANT HOUSE
OPERATIONAL AND MAINTENANCE TOOLS
BILL No. | TOOLS & EQUIPMENT
| Sub-Total 1 | 0
| Allow for 5% contingency | 0
| Sub-Total 2 | 0
| Allow for 18% VAT | 0
| TOTAL | 0

## M-G-1
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-G-1
DESCRIPTION: | GENERAL ITEMS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Contractual Requirements
A110.1 | Performance security clause | sum | 0 |  | Rate only
A110.2 | Advance payment guarantee | sum | 0 |  | Rate only
A120.1 | Insurance of works covering all installations during and up to 28 days after the end of the defects liability period | sum | 1 |  | 0
A120.2 | Third party insurance | sum | 1 |  | 0
A120.3 | Insurance of Contractors Equipment | sum | 1 |  | 0
Specified Requirements
Site Offices and Housing
A211.1 | Establishment and removal of offices for the Engineer's staff | sum | 0 |  | Rate only
A211.2 | Provision of rented office accommodation for the Engineer's staff before establishment of site offices | month | 0 |  | Rate only
A211.3 | Provision of rented accommodation for the Engineer's staff (2No unit) | month | 0 |  | Rate only
A211.4 | Maintenance of offices for the Engineer's staff including provision and payment of utility services | month | 0 |  | Rate only
A211.5 | Maintenance of housing accommodationfor the Engineer's staff (1No unit) including provision and payment of utility services | months | 0 |  | Rate only
Services for the Engineer's staff
Transport Services
A221.1 | Supply of brand new, latest model , 125 C.C , all terrain Motor cycles, with helmets and riding gear; | nr | 0 |  | Rate only
A221.2 | Provide for the maintenance of the motor cycles including fueling, routine service and repairs for the whole Contract period. | Km | 0 |  | Rate only
|  |  |  | Carried to Collection | 0
Communication
A222.1 | Establish communication system and dedicated email (mobile, wireless or leased line) system for the Engineer's office | sum | 0 |  | Rate only
A222.2 | Maintenance of communication system and dedicated email (mobile, wireless or leased line) system for the Engineer's office | month | 0 |  | Rate only
A222.3 | Provision of 1No. Mobile phone handsets for use by the Engineer's staff | nr | 0 |  | Rate only
A222.4 | Payment of monthly services bills on mobile calls and data | months | 0 |  | Rate only
Equipment for use by the Engineer's staff
A231.1 | Provision of office furniture & equipment for the Engineer | sum | 0 |  | Rate only
A231.2 | Maintenance of office furniture & equipment for the Engineer | month | 0 |  | Rate only
A233 | Provision of surveying equipment for use by the Engineer | month | 0 |  | Rate only
A234 | Provision of office stationary & office consumables for use in the Engineer's office | month | 0 |  | Rate only
Attendance upon the Engineer's staff
A240 | Provision of the services of the Office Assistant | months | 0 |  | Rate only
A241 | Provision of the services of a permanent driver for use by Engineer's staff | months | 0 |  | Rate only
A242 | Provision of services of 1No survey chainmen | months | 0 |  | Rate only
A243 | Provision of services of a laboratory assistant | months | 0 |  | Rate only
Testing works
Testing of Materials
A250.1 | Testing of pressure pipes at Uganda Natioal Bureau of Standards | sum | 1 |  | Rate only
A250.2 | Testing of concrete test cubes at ministry of works materials laboratories | sum | 1 |  | Rate only
A250.3 | Testing and certification of mechanical and electrical systems | sum | 1 |  | Rate only
|  |  |  | Carried to Collection | 0
Testing and Commissioning works
Pipeline pressure testing
A260.1 | Pressure testing of and sterilisation of water mains as per specifications: uPVC nominal bore not exceeding OD 110mm; maximum test pressure not exceeding twice the pipe's pressure rating. | km | 3.79 |  | Rate only
A260.2 | Pressure testing of and sterilisation of water mains as per specifications:HDPE pipes nominal bore ND32-79.2mm and ND 99.4-; maximum test pressure not exceeding 1.5times the pipe's pressure rating. | Km | 7.126 |  | Rate only
Water tightness testing of Tanks
A260.3 | Pressed steel sectional tanks | Sum | 1 |  | 0
A260.4 | Testing and certification of mechanical and electrical systems | Sum | 1 |  | Rate only
A260.5 | Test running and Commissioning of water supply system, inclusive of full operations of the water supply system for 30 consecutive days, preparation of daily reports on the operations that comprise of the amount of water pumped, quantity of chemicals utilised, hours of pumping, energy consumed, at least 6No off site detailed water quality tests etc as directed by the Engineer. These shall form part of the operation and maintenance manual and As-Built drawings that shall be submitted to the Employer. Training Private Operator's staff in basic operation and maintenance procedures of all plant and equipment supplied as per the technical specifications and to the Engineer's approval shall form part of this activity | sum | 1 |  | Rate only
Temporary Works
A279.1 | Establishment & removal of site sign-boards | nr | 1 |  | 0
A279.2 | Maintenance of site sign-boards until the issue of the Taking-over Certificate | month | 2 |  | Rate only
A279.3 | Provision for work in water affected areas, including dewatering of sites and wrk areas, all temporary works, protection, access etc to ensure works are completed as specified. | sum | 1 |  | Rate only
A260.7 | Supply and installation of permanent labels made of engraved granite on the various installations as directed by the Engineer | nr | 2 |  | Rate only
Provisional Sums
A420.1 | Allow for relocation of existing services including repair of damage caused to all existing services (e.g. pipes, cables, drains, e.t.c) including emergency and/or permanent diversion of all kinds of roads and rectification of damaged property made on behalf of the employer, , including all administrative costs | sum | 1 |  | Rate only
|  |  |  | Carried to Collection | 0
A420.2 | Allow for Client's project specific administration costs, factory visits and testing for specialised equipment, factory acceptance tests & witnessing expenses | sum | 0 |  | Rate only
A420.3 | Allow for Environmental protection activities such as tree planting of at least 10 pcs at the reservoir station in consultation with the District Environmental Officer and Client's representative | Sum | 1 |  | 0
A420.4 | Water connection surveys and registration by Others (Verification of applications for consumer connections) | sum | 0 |  | Rate only
A420.5 | Allow for stakeholder sensitisation on cross cutting issues (HIV/AIDs, Sexual Exploitation and Abuse, PWDs, Gender inclusion and equality, Nutrition, Environmental awareness and good governance) and their integration in implementation through trainings and community campaigns by others, to include the respective district and subcounty offices/office bearers | sum | 0 |  | Rate only
A420.6 | Allow for Operation and Maintenance training for all successfully verified and connected consumers and leaders through community workshops by others, including all administrative costs | sum | 0 |  | Rate only
A420.7 | Contractor's charges and profits associated with administration of bill items, A221.1, A420.1 to A420.6 (Maximum 20%) | % | 0%
Recorded Documents
A260.8 | Prepare operation and maintenance manuals as per specifications and to the Engineer's approval | sum | 1 |  | Rate only
A260.9 | Prepare ''as-built'' or record drawings as per specifications and to Engineer's approval | sum | 1 |  | Rate only
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page B-Z-G-1/1 |  |  |  | 0
| Collection, Page B-Z-G-1/2 |  |  |  | 0
| Collection, Page B-Z-G-1/3 |  |  |  | 0
| Collection, Page B-Z-G-1/4 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## M- G-2
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-G-2
DESCRIPTION: | METHOD RELATED CHARGES
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
METHOD RELATED CHARGES
NKA G-2.1 | Mobilisation on site | sum | 1 |  | 0
NKA G-2.2 | Demobilise on completion of the Works | sum | 1 |  | 0
A311.1 | Supply and/or erect Contractor's site offices. | sum | 1 |  | 0
A311.2 | Maintain Contractor's site offices, including all services | months | 3 |  | 0
A311.3 | Remove Contractor's site offices on completion of the Works | sum | 1 |  | 0
In the following pages, may be entered in accordance with Section 7 of CESMM4. These must distinguish between fixed and time related charges.
Fixed charge items
NKA G-2.3 | Storage sheds and workshop | Sum | 1 |  | 0
Time related charge items
NKA G-2.4 | Supervision | Month | 3 |  | 0
|  |  |  | Carried to Summary | 0

## M-G-3
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-G-3
DESCRIPTION: | DAYWORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
DESCRIPTION
Personnel
A411.1 | Working ganger | hr | 10
A411.2 | Artisan | hr | 10
A411.3 | Semi-skilled | hr | 10
A411.4 | Unskilled | hr | 10
A411.5 | Driver for light vehicle | hr | 10
A411.6 | Driver for heavy vehicle | hr | 7
A411.7 | Operator for heavy equipment | hr | 7
Materials
A413.1 | Ordinary Cement in 50 kg bags | t | 1
A413.2 | Coarse aggregate for concrete. | m³ | 1
A413.3 | Fine aggregate for concrete. | m³ | 0.5
A413.4 | Water for concrete | m³ | 10
A413.5 | Sand for building | m³ | 0.5
A413.6 | Sand for plaster | m³ | 0.5
A413.7 | Bricks for building. | nr | 5000
A413.8 | Concrete blocks for building, 225 mm for building,150 mm thick | m² | 0.5
A413.9 | Concrete blocks for building, 150 mm thick. | m² | 0.5
A413.10 | Hydrated lime for building 150 mm thick. | kg | 1
A413.11 | Timber, sawn. | m³ | 0.5
A413.12 | Timber wrot. | m³ | 0.5
High yield steel reinforcement:-
A413.13 | 8-10 mm dia | kg | 16
High yield steel reinforcement:-
A413.14 | 12-16 mm dia. | kg | 16
High yield steel reinforcement:-
A413.15 | 20-25 mm dia. | kg | 2
A413.16 | Steel reinforcement fabric S reference:A252 | m² | 5
A413.17 | Hardcore filling | m³ | 2
A413.18 | Topsoil delivered to site | m³ | 2
CONTRACTOR'S EQUIPMENT
A415.1 | Road vehicles:Pick-up,1 1/2t. | hr | 5
Road vehicles: Lorries:
A415.1 | Flat-5t capacity | hr | 4
A415.2 | Flat-10t capacity | hr | 4
Tipping :
A415.3 | 5t capacity | hr | 5
A415.4 | 10t capacity | hr | 5
Water tankers with pump and hoses:
A415.5 | 5,000 capacity. | hr | 2
Carried to Collection
Excavation, face shovel or dragline:
A415.6 | 0.25 m3 bucket. | hr | 5
A415.7 | 0.5m3 bucket. | hr | 3
A415.8 | 1.0m3 bucket. | hr | 3
Tractors:
A415.9 | rubber tyred with trailer, 75 kw.tracked including bull and angle dozer with ripper: | hr | 0.5
A415.10 | 150 kw. | hr | 0.5
A415.11 | 200 kw | hr | 0.5
A415.12 | 250 kw. | hr | 0.5
Rollers:
A415.13 | Manual, 250 kg | hr | 0.5
A415.14 | vibratory, self, propelled, 1500 kg. | hr | 0.5
Concrete mixers with weigh batchers and loading hoppers:
A415.15 | 300 lit capacity. | hr | 6
Concrete vibrator, pneumatic with hoses:
A415.16 | poker type, 50 mm | hr | 1
Bar bending and shearing machines:
A415.17 | bending:-
| (1) hand operated. | hr | 0.5
A415.18 | shearing:-
| (1) hand operated | hr | 0.5
Air compressor, mobile with 5m of hose and steels with:
A415.19 | 1 breaker. | hr | 10
A415.20 | 2 breakers. | hr | 10
Mobile electricity generating sets, 240v, 1 ph, 50 Hz:
A415.21 | 5 kvA | hr | 2
A415.22 | 10 kvA | hr | 2
COLLECTION
Collection, Page M-G-3/1
Collection, Page M-G-3/2
|  |  |  | Carried to Summary | 0

## M-W-4-RT
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
Bill No. | M- W-4
DESCRIPTION: | STORAGE RESERVOIR TANK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE Ushs | AMOUNT Ushs
Preamble
The works under this bill are covered under Part 2 of the Particular Specifications.
SUBSTRUCTURE
Site Clearance
D100 | Clear the site of bushes, scrub and undergrowth and vegetable soil to allow for proper and accurate setting out | ha | 0.09 |  | 0
Excavations for Foundations
Topsoil
E410 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m³ | 6.3504 |  | 0
Ordinary Soil
Excavation for foundations (Raft foundation), in material other than topsoil, rock or artificial hard material, commencing surface is the stripped ground level
E334 | Depth 1-2 m | m³ | 67.2 |  | 0
Rock
Excavation for foundations, in rock, commencing surface is the stripped ground level
E335 | Depth 0.5-1.0 m | m³ | 2.016 |  | 0
Disposal of Excavated Material
Disposal of excavated material to sites as shown in the site layout and as specified and as directed by the Engineer
E531 | Soil | m³ | 45.5504 |  | 0
E533 | Rock | m³ | 2.016 |  | 0
Carried to Collection |  |  |  |  | 0
Filling
Structures
Filling by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | CM | 44.8 |  | 0
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to reservoir area and compacted to 98% MOD AASHTO | CM | 44.8 |  | 0
Provision of Hardcore
E810 | Provision and placement of 300 mm thick hardcore base for the tank footings | SM | 16.8 |  | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F131 | 10 mm aggregate | CM | 2.8 |  | 0
Grade C25
Designed mix, grade C15 concrete, to BS 5328, with ordinary Portland cement to BS 12, aggregate to BS 882, for the following aggregate sizes
F151 | 10 mm aggregate | CM | 40.218 |  | 0
Carried to Collection |  |  |  |  | 0
Placing Mass Concrete
Blinding
Placing blinding concrete, grade C15 of the following thickness
F512 |  | CM | 2.8 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete, grad C25, for column base footings of the following thickness
F522 |  | CM | 16.368 |  | 0
Dwarf walls
Placing reinforced concrete, grade C25, for columns of the following thickness
F523 |  | CM | 23.85 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G245 | Width exceeding 1.22 m | SM | 193 |  | 0
Reinforcement
High Yeild Steel
High yeild square twisted or ribbed bars to BS 4449 and of the following sizes
G525 | Nominal size T12 mm | kg | 1123.9111 |  | 0
G525 | Nominal size T10 mm | kg | 94.2942 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G812 | With steel float finish | m² | 193 |  | 0
| Carried to Collection |  |  |  | 0
PIPEWORK - FITTINGS AND VALVES
Cast or Spun Iron Pipe Fittings external epoxy coated to AWWA C213
Bends
Ductile iron all flanged 90 degree bend, to BS 4772, flanges to BS 4504, all to PN 16, cement mortar lined, and of the following sizes
J311.2 | DN100 | nr | 6 |  | 0
Junctions and Branches
All flanged tee to BS 4346, flanges to BS 4504, all to PN 16, and of the following sizes
J321.1 | DN100 | nr | 1 |  | 0
Double Collars
Viking Johnson or similar, wide range coupling to fit all pipe spigots to PN 16, and of the following sizes
J341.1 | DN100 | nr | 20 |  | 0
Adaptors
Flanged adaptor Maxi Type or similar wide range adaptor to fit pipe spigots, flanes to BS 4505, all to PN 16 and of the following sizes
J351.1 | DN100 | nr | 6 |  | 0
Straight Specials
Ductile iron double flanged pipe, to BS 4772, flanges to BS 4504, cement mortar lined, all to PN 16 and of the following sizes
J381.1 | DN 100 not exceeding 6.0 m | nr | 4 |  | 0
Strainer
Flanged outlet pipe strainer, to BS 4772, flanges to BS 4504, all to PN 16, cement mortar lined, and of the following sizes
J491.1 | DN100 | nr | 3 |  | 0
Gate Valves: Hand Operated
All flanged CI gate valves to BS 5150, flanges to BS 4505, all to PN 16 for operation by tee key, with extension spindle not exceeding 1.5 metres long, and of the following sizes
J811.1 | DN100 | nr | 4 |  | 0
Carried to Collection |  |  |  |  | 0
Ball Float Valves
Flanged Balanced ball float valve, flanges to BS 4505, all to PN 16
J891.1 | DN100 | nr | 1 |  | 0
Bulk Flow Meter
"Woltman" Helix Type Bulk Flow Meter inclusive of all couplings, adaptors, steel pipe distance pieces, CI valves, thrust blocks, etc and all other fittings to make the installation complete, as specified, all fittings to PN 16, including lockable vented blockwork chamber with cast in valve surface boxes, and on the following main pipe sizes
J991.1 | DN 100 | nr | 2 |  | 0
PIPEWORK - MANHOLES AND PIPEWORK
Manholes
Blockwork Manhole
Blockwork chamber complete with C20 concrete base, vented lockable manhole cover, valve surface boxes, galvanised step irons, as specified in the drawings, and of the following depths
K171 | Depth not exceeding 1.5 m | nr | 3 |  | 0
Other Chambers
In situ Concrete Chambers
Washout out fall structure, complete including flap valve, all fittings and pipework necessary to complete installation, as specified in drawings, and of the following depths; all fittings and pipework to PN 16
K231 | Depth not exceeding 1.5 m | nr | 1 |  | 0
Supply and construct grouted stone pitching using mortar mix 1:4, include 50mm thick coping using 1:2:4 concrete mix on top of the stone pitching of same width as the wall thickness for drains of cross section
K491 | Cross section area 0.5-1.0 m2 | m | 20 |  | 0
Carried to Collection |  |  |  |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | CM | 2 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - DN 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5 m | nr | 4 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 4 |  | 0
K820.2 | Marker posts for bulk meters | nr | 2 |  | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 300 mm ND | m | 20 |  | 0
Carried to Collection |  |  |  |  | 0
MISCALLANEOUS WORKS
Supply and Install cold pressed galvanised steel sectional tank with external flanges and pitched cover with 1No. 1m wide access way, solenoid float switch, water level indicator (scale in cubic metres) and plates with inlet, outlet, washout and overflow connection complete with access points, ventilators (4 nr), and internal and external access ladders with safety hoops, inclusive of painting, finishes and all necessary accessories to installation complete as specified and detailed in the drawings; to the Engineer's satisfaction. All tank accessories shall be of hot dipped galvanised steel. All to the Engineer's satisfaction Design criteria; pressed steel sections to BS 1564, Hot rolled sections to BS 4360, Bolts and nuts to BS 5950, structural steel to BS 5950, dead and live load analysis to BS 6399; Complete with all the necessary pipe manfold inclusive of Tees, Gate Valves, Bends, rise pipe into the reserviour and all necessary pipe work to ensure proper installation.
N287 | Reservoir: 75 m3 nominal capacity placed on a 1.5 m high concrete pedestal | nr | 1 |  | 0
0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | CM | 144 |  | 0
ROADS AND PAVINGS
Sub-Bases
Heavy duty , C30 Concrete interlocking pavers, thickness 100 - 125mm for walkways, access and parking areas;
R114 | Concrete pavers | m² | 0 |  | 0
Surfacing
R331 | Wearing course, of slurry doube bitumen seal as specified , including sub - base preparation, importation of approved murrum, level, spread and compacted, all to receive the bitumen layer | m² | 0 |  | 0
Kerbs
Construct Kerbs of ore-cast concrete to BS 7263 of cross section area 0.05-0.1 m2 to the following alignment
R611 | Straight or curved to a radius exceeding 12 m | m | 0 |  | 0
0
Carried to Collection |  |  |  |  | 0
COLLECTION
| Collection, Page M-W-4/1 |  |  |  | 0
| Collection, Page M-W-4/2 |  |  |  | 0
| Collection, Page M-W-4/3 |  |  |  | 0
| Collection, Page M-W-4/4 |  |  |  | 0
| Collection, Page M-W-4/5 |  |  |  | 0
| Collection, Page M-W-4/6 |  |  |  | 0
| Collection, Page M-W-4/7 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## M-W-5-RTW
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-W-5
DESCRIPTION: | STORAGE RESERVOIR SITE WORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for works | ha | 0.0144 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 0 |  | Rate only
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 0 |  | Rate only
EARTHWORKS
General Excavation
Topsoil
E410 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m³ | 21.6 |  | 0
Ordinary Soil
General excavation for foundation, road works and parking area, in material other than topsoil, rock or artificial hard material, commencing surface is the stripped ground level
E324 | Maximum depth 0.25 - 0.5 m | m³ | 0 |  | Rate only
Rock
Excavation for foundations, in rock, commencing surface is the stripped ground level
E335 | Depth 0.5 - 1.0 m | m³ | 0 |  | Rate only
|  |  |  | Carried to Collection | 0
Disposal of Excavated Material
Disposal of excavated material to sites as shown in the site layout and as specified and as directed by the Engineer
E531 | Soil | m³ | 21.6 |  | 0
E533 | Rock | m³ | 0 |  | Rate only
Filling
Structures
Filling by methods specified and to depths as shown in the drawings with the following materials
E614 | Selected excavated material other than topsoil, rock or artificial hard material | m³ | 0 |  | Rate only
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to reservoir area and compacted to 98% MOD AASHTO | m³ | 4.9 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 144 |  | 0
| ROADS AND PAVINGS |  |  |  | 0
0
| Sub-Bases |  |  |  | 0
0
| Heavy duty , C30 Concrete interlocking pavers, thickness 100 - 125mm for walkways, access and parking areas; |  |  |  | 0
0
R114 | concrete Pavers | m² | 0 |  | Rate only
0
| Surfacing |  |  |  | 0
0
R331 | Wearing course, of slurry doube bitumen seal as specified , including sub - base preparation, importation of approved murrum, level, spread and compacted, all to receive the bitumen layer | m² | 0 |  | Rate only
0
| Kerbs |  |  |  | 0
| Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment |  |  |  | 0
0
R611 | Straight or curved to a radius exceeding 12 m | m | 0 |  | Rate only
0
| MISCELLANEOUS WORKS |  |  |  | 0
0
| Fences |  |  |  | 0
0
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with galvanised razor wire on top, anchored into C20 Concrete dwarf wall as per drawings, height 2.6-2.8 m | m | 48 |  | 0
0
| Gates |  |  |  | 0
0
| Metal field sliding gate , Fabricated in 80 x 40 x 4 RHS Sections all to BS 3470 of the following widths and spray painted with 3 coats gloss paint; |  |  |  | 0
0
X235 | with 900mm wide pedestrain gate-metal grill | nr | 1 |  | 0
Stone Chippings
R118 | Supply and spread approved stone chippings (16mm aggregates) on compacted surfaces | m² | 0 |  | Rate only
0
0
COLLECTION
| Collection, Page M-W 5/1 |  |  |  | 0
| Collection, Page M-W 5/2 |  |  |  | 0
| Collection, Page M-W 5/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0