## Cover
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BIDDER'S ESTIMATE - Lot 2
Bidder's Estimate for Muwayo TC -piped water supply scheme

## Preamble
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BIDDER'S ESTIMATE - Lot 2
Preamble: This BoQ relates to the proposed construction of the mini-piped water scheme at Muwayo TC. The BoQ should be read together with the drawings and the technical specifications. The project consists of a pumping station, the transmission pipeline, storage tanks and distribution pipelines. Water is pumped from a borehole of yield 14.4m3/hour yield using solar powered pump. The water is pumped to a reservoir approx 2.4km from the borehole to a reservoir of 75m3 , elevated 1.5m on a pedestal. The project has allowed for 15 PSP for water collection.
Lot 2 scope: This covers works for the pumping station, the transmission and distribution pipelines, intensification networks and all civil works and as described in the BoQ, excluding reservior station works and installation of PSPs.

## Grand Summary
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BIDDER'S ESTIMATE - Lot 2
GRAND SUMMARY
Bill No | Bill Description | INVESTMENT COST
GENERAL
M-G-1 | GENERAL ITEMS | 0
M-G-2 | METHOD RELATED CHARGES | 0
M-G-3 | DAYWORKS
| SUB-TOTAL | 0
WATER SUPPLY AND EQUIPMENT
MUWAYO WATER SUPPLY NETWORK
M-W-1 | MUWAYO BOREHOLE PUMP STATION DEVELOPMENT | 0
M-W-2 | MUWAYO PUMP AND GUARD HOUSE | 0
M-W-3 | MUWAYO PUMPING MAINS | 0
M- W-4 | STORAGE RESERVOIR TANK | 0
M-W-5 | STORAGE RESERVOIR SITE WORKS | 0
M- W-6 | MUWAYO DISTRIBUTION NETWORK | 0
M-W-7 | INTENSIFICATION NETWORKS
M-W-8 | CONSUMER CONNECTIONS | 0
M-W-9 | MECHANICAL & ELECTRICAL WORKS | 0
GENERAL CONSTRUCTION WORKS
M-W-10 | GUARD AND PUMP ATTENDANT HOUSE | 0
OPERATIONAL AND MAINTENANCE TOOLS
BILL No. | TOOLS & EQUIPMENT
| Sub-Total 1 | 0
| Allow for 5% contingency | 0
| Sub-Total 2 | 0
| Allow for 18% VAT | 0
| TOTAL | 0

## M-G-1
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-G-1
DESCRIPTION: | GENERAL ITEMS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Contractual Requirements
A110.1 | Performance security clause | sum | 0 |  | Rate only
A110.2 | Advance payment guarantee | sum | 0 |  | Rate only
A120.1 | Insurance of works covering all installations during and up to 28 days after the end of the defects liability period | sum | 1 |  | 0
A120.2 | Third party insurance | sum | 1 |  | 0
A120.3 | Insurance of Contractors Equipment | sum | 1 |  | 0
Specified Requirements
Site Offices and Housing
A211.1 | Establishment and removal of offices for the Engineer's staff | sum | 0 |  | Rate only
A211.2 | Provision of rented office accommodation for the Engineer's staff before establishment of site offices | month | 0 |  | Rate only
A211.3 | Provision of rented accommodation for the Engineer's staff (2No unit) | month | 0 |  | Rate only
A211.4 | Maintenance of offices for the Engineer's staff including provision and payment of utility services | month | 0 |  | Rate only
A211.5 | Maintenance of housing accommodationfor the Engineer's staff (1No unit) including provision and payment of utility services | months | 0 |  | Rate only
Services for the Engineer's staff
Transport Services
A221.1 | Supply of brand new, latest model , 125 C.C , all terrain Motor cycles, with helmets and riding gear; | nr | 0 |  | Rate only
A221.2 | Provide for the maintenance of the motor cycles including fueling, routine service and repairs for the whole Contract period. | Km | 0 |  | Rate only
|  |  |  | Carried to Collection | 0
Communication
A222.1 | Establish communication system and dedicated email (mobile, wireless or leased line) system for the Engineer's office | sum | 0 |  | Rate only
A222.2 | Maintenance of communication system and dedicated email (mobile, wireless or leased line) system for the Engineer's office | month | 0 |  | Rate only
A222.3 | Provision of 1No. Mobile phone handsets for use by the Engineer's staff | nr | 0 |  | Rate only
A222.4 | Payment of monthly services bills on mobile calls and data | months | 0 |  | Rate only
Equipment for use by the Engineer's staff
A231.1 | Provision of office furniture & equipment for the Engineer | sum | 0 |  | Rate only
A231.2 | Maintenance of office furniture & equipment for the Engineer | month | 0 |  | Rate only
A233 | Provision of surveying equipment for use by the Engineer | month | 0 |  | Rate only
A234 | Provision of office stationary & office consumables for use in the Engineer's office | month | 0 |  | Rate only
Attendance upon the Engineer's staff
A240 | Provision of the services of the Office Assistant | months | 0 |  | Rate only
A241 | Provision of the services of a permanent driver for use by Engineer's staff | months | 0 |  | Rate only
A242 | Provision of services of 1No survey chainmen | months | 0 |  | Rate only
A243 | Provision of services of a laboratory assistant | months | 0 |  | Rate only
Testing works
Testing of Materials
A250.1 | Testing of pressure pipes at Uganda Natioal Bureau of Standards | sum | 1 |  | 0
A250.2 | Testing of concrete test cubes at ministry of works materials laboratories | sum | 1 |  | 0
A250.3 | Testing and certification of mechanical and electrical systems | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Testing and Commissioning works
Pipeline pressure testing
A260.1 | Pressure testing of and sterilisation of water mains as per specifications: uPVC nominal bore not exceeding OD 110mm; maximum test pressure not exceeding twice the pipe's pressure rating. | km | 3.79 |  | 0
A260.2 | Pressure testing of and sterilisation of water mains as per specifications:HDPE pipes nominal bore ND32-79.2mm and ND 99.4-; maximum test pressure not exceeding 1.5times the pipe's pressure rating. | Km | 7.126 |  | 0
Water tightness testing of Tanks
A260.3 | Pressed steel sectional tanks | Sum | 1 |  | Rate only
A260.4 | Testing and certification of mechanical and electrical systems | Sum | 1 |  | 0
A260.5 | Test running and Commissioning of water supply system, inclusive of full operations of the water supply system for 30 consecutive days, preparation of daily reports on the operations that comprise of the amount of water pumped, quantity of chemicals utilised, hours of pumping, energy consumed, at least 6No off site detailed water quality tests etc as directed by the Engineer. These shall form part of the operation and maintenance manual and As-Built drawings that shall be submitted to the Employer. Training Private Operator's staff in basic operation and maintenance procedures of all plant and equipment supplied as per the technical specifications and to the Engineer's approval shall form part of this activity | sum | 1 |  | 0
Temporary Works
A279.1 | Establishment & removal of site sign-boards | nr | 1 |  | 0
A279.2 | Maintenance of site sign-boards until the issue of the Taking-over Certificate | month | 6 |  | 0
A279.3 | Provision for work in water affected areas, including dewatering of sites and wrk areas, all temporary works, protection, access etc to ensure works are completed as specified. | sum | 1 |  | 0
A260.7 | Supply and installation of permanent labels made of engraved granite on the various installations as directed by the Engineer | nr | 2 |  | 0
Provisional Sums
A420.1 | Allow for relocation of existing services including repair of damage caused to all existing services (e.g. pipes, cables, drains, e.t.c) including emergency and/or permanent diversion of all kinds of roads and rectification of damaged property made on behalf of the employer, , including all administrative costs | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
A420.2 | Allow for Client's project specific administration costs, factory visits and testing for specialised equipment, factory acceptance tests & witnessing expenses | sum | 0 |  | Rate only
A420.3 | Allow for Environmental protection activities such as tree planting at the intake and at the pipeline routing/road reserves in consultation with the District Environmental Officer and Client's representative | Sum | 1 |  | 0
A420.4 | Water connection surveys and registration by Others (Verification of applications for consumer connections) | sum | 0 |  | Rate only
A420.5 | Allow for stakeholder sensitisation on cross cutting issues (HIV/AIDs, Sexual Exploitation and Abuse, PWDs, Gender inclusion and equality, Nutrition, Environmental awareness and good governance) and their integration in implementation through trainings and community campaigns by others, to include the respective district and subcounty offices/office bearers | sum | 0 |  | Rate only
A420.6 | Allow for Operation and Maintenance training for all successfully verified and connected consumers and leaders through community workshops by others, including all administrative costs | sum | 0 |  | Rate only
A420.7 | Contractor's charges and profits associated with administration of bill items, A221.1, A420.1 to A420.6 (Maximum 20%) | % | 0%
Recorded Documents
A260.8 | Prepare operation and maintenance manuals as per specifications and to the Engineer's approval | sum | 1 |  | 0
A260.9 | Prepare ''as-built'' or record drawings as per specifications and to Engineer's approval | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page B-Z-G-1/1 |  |  |  | 0
| Collection, Page B-Z-G-1/2 |  |  |  | 0
| Collection, Page B-Z-G-1/3 |  |  |  | 0
| Collection, Page B-Z-G-1/4 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## M- G-2
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-G-2
DESCRIPTION: | METHOD RELATED CHARGES
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
METHOD RELATED CHARGES
NKA G-2.1 | Mobilisation on site | sum | 1 |  | 0
NKA G-2.2 | Demobilise on completion of the Works | sum | 1 |  | 0
A311.1 | Supply and/or erect Contractor's site offices. | sum | 1 |  | 0
A311.2 | Maintain Contractor's site offices, including all services | months | 3 |  | 0
A311.3 | Remove Contractor's site offices on completion of the Works | sum | 1 |  | 0
In the following pages, may be entered in accordance with Section 7 of CESMM4. These must distinguish between fixed and time related charges.
Fixed charge items
NKA G-2.3 | Storage sheds and workshop | Sum | 1 |  | 0
Time related charge items
NKA G-2.4 | Supervision | Month | 3 |  | 0
|  |  |  | Carried to Summary | 0

## M-G-3
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-G-3
DESCRIPTION: | DAYWORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
DESCRIPTION
Personnel
A411.1 | Working ganger | hr | 10
A411.2 | Artisan | hr | 10
A411.3 | Semi-skilled | hr | 10
A411.4 | Unskilled | hr | 10
A411.5 | Driver for light vehicle | hr | 10
A411.6 | Driver for heavy vehicle | hr | 7
A411.7 | Operator for heavy equipment | hr | 7
Materials
A413.1 | Ordinary Cement in 50 kg bags | t | 1
A413.2 | Coarse aggregate for concrete. | m³ | 1
A413.3 | Fine aggregate for concrete. | m³ | 0.5
A413.4 | Water for concrete | m³ | 10
A413.5 | Sand for building | m³ | 0.5
A413.6 | Sand for plaster | m³ | 0.5
A413.7 | Bricks for building. | nr | 5000
A413.8 | Concrete blocks for building, 225 mm for building,150 mm thick | m² | 0.5
A413.9 | Concrete blocks for building, 150 mm thick. | m² | 0.5
A413.10 | Hydrated lime for building 150 mm thick. | kg | 1
A413.11 | Timber, sawn. | m³ | 0.5
A413.12 | Timber wrot. | m³ | 0.5
High yield steel reinforcement:-
A413.13 | 8-10 mm dia | kg | 16
High yield steel reinforcement:-
A413.14 | 12-16 mm dia. | kg | 16
High yield steel reinforcement:-
A413.15 | 20-25 mm dia. | kg | 2
A413.16 | Steel reinforcement fabric S reference:A252 | m² | 5
A413.17 | Hardcore filling | m³ | 2
A413.18 | Topsoil delivered to site | m³ | 2
CONTRACTOR'S EQUIPMENT
A415.1 | Road vehicles:Pick-up,1 1/2t. | hr | 5
Road vehicles: Lorries:
A415.1 | Flat-5t capacity | hr | 4
A415.2 | Flat-10t capacity | hr | 4
Tipping :
A415.3 | 5t capacity | hr | 5
A415.4 | 10t capacity | hr | 5
Water tankers with pump and hoses:
A415.5 | 5,000 capacity. | hr | 2
Carried to Collection
Excavation, face shovel or dragline:
A415.6 | 0.25 m3 bucket. | hr | 5
A415.7 | 0.5m3 bucket. | hr | 3
A415.8 | 1.0m3 bucket. | hr | 3
Tractors:
A415.9 | rubber tyred with trailer, 75 kw.tracked including bull and angle dozer with ripper: | hr | 0.5
A415.10 | 150 kw. | hr | 0.5
A415.11 | 200 kw | hr | 0.5
A415.12 | 250 kw. | hr | 0.5
Rollers:
A415.13 | Manual, 250 kg | hr | 0.5
A415.14 | vibratory, self, propelled, 1500 kg. | hr | 0.5
Concrete mixers with weigh batchers and loading hoppers:
A415.15 | 300 lit capacity. | hr | 6
Concrete vibrator, pneumatic with hoses:
A415.16 | poker type, 50 mm | hr | 1
Bar bending and shearing machines:
A415.17 | bending:-
| (1) hand operated. | hr | 0.5
A415.18 | shearing:-
| (1) hand operated | hr | 0.5
Air compressor, mobile with 5m of hose and steels with:
A415.19 | 1 breaker. | hr | 10
A415.20 | 2 breakers. | hr | 10
Mobile electricity generating sets, 240v, 1 ph, 50 Hz:
A415.21 | 5 kvA | hr | 2
A415.22 | 10 kvA | hr | 2
COLLECTION
Collection, Page M-G-3/1
Collection, Page M-G-3/2
|  |  |  | Carried to Summary | 0

## M-W-1-PS
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-W-1
DESCRIPTION: | MUWAYO BOREHOLE PUMP STATION DEVELOPMENT
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE Ushs | AMOUNT Ushs
Preamble:
The works under this bill are covered under Part 3 of the Particular Specifications
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance including clearance of access road to the site. | ha | 0.105 |  | 0
Trees
Cut and dispose of trees of the following diameter; include for grabbing up the roots and back filling the hole left with topsoil.
D210 | Girth: 500 mm - 2 m | nr | 5 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diamter 150-500 mm | nr | 2 |  | 0
| Landscaping |  |  |  | 0
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 1050 |  | 0
0
E820 | Allow for Planting of approved passcurum grass, watering & maintenance for at least six months | m² | 599 |  | 0
PAVINGS
Stone Chippings
R118 | Supply and spread approved stone chippings (16mm aggregates) on compacted surfaces under the solar panels | m² | 162 |  | 0
| Kerbs |  |  |  | 0
R711 | Construct Kerbs of pre-cast concrete to BS 7263 of cross section area 0.05-0.1 m² to the following alignment Straight or curved to a radius exceeding 12 m | m | 112 |  | 0
Walkways and Compounds
R911 | Concrete (C20) paved walkway in 600 x 600 x 50 mm thick sections and/or pavers as per Engineers instruction.; include sand bedding, earthworks, jointing and concrete edge protection | m² | 35 |  | 0
Fences
X135 | 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 12.5 to BS 1722, with triple row of barbed wire on top, anchored into blockwork dwarf wall as per drawings, height 2-2.5 m | m | 130 |  | 0
Gates
Supply and complete installation of painted metal field gate to BS 3470 include C25 reinforced concrete pad foundations and columns; and of the following widths
X236 | Width 3.5 m, double leaf complete | nr | 1 |  | 0
Carried to Collection |  |  |  |  | 0
COLLECTION
| Collection, Page M-W-1/1 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## M-W-2-PH
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-W-2
DESCRIPTION: | MUWAYO PUMP HOUSE
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance including clearance of access road to the site | ha | 0 |  | Rate only
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 0 |  | Rate only
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 0 |  | Rate only
EARTHWORKS
Excavation for foundations
Topsoil
E310 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m3 | 2.5 |  | 0
All Materials other than top soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level
E323 | Depth for Buildings 0-1.5m | m3 | 5.5 |  | 0
Excavation Ancillaries
E596 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
E597 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
|  |  |  | Carried to Collection | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
E615 | Selected imported granular material other than topsoil, rock or artificial hard material to pump house area and compacted to 98% MOD AASHTO | m³ | 4.8 |  | 0
E645 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 4.8 |  | 0
E647 | 200mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 4.8 |  | 0
Landscaping
E810 | Turfing for lawns inside fenced off compound; include filling with excavated topsoil, levelling and the preparation of the surfaces. Include the planting of water friendly trees as recommended by the Engineer | m² | 0 |  | Rate only
IN SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C15
Designed mix, grade C15 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F141 | 10mm aggregate | m³ | 3.98 |  | Rate only
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
F151 | 10mm aggregate | m³ | 1.7 |  | Rate only
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C20, of the following thickness
F522 | Thickness 150-300mm | m³ | 2.3 |  | 0
|  |  |  | Carried to Collection | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and plinth of the following thickness
F622 | Thickness 150-300mm | m³ | 1.7 |  | 0
Suspended Slabs
Placing reinforced concrete, grade C25, for false slab (ceiling) of the following thickness
F631 | Thickness not exceeding 150mm | m³ | 1.68 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
F662 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.33 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork to floor and pump houses of the following width
G214 | Width: 0.4-1.22m; to false slab soffits | m² | 37.9 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
G244.1 | Width: 0.4-1.22m; to floor and plinth | m² | 5.7 |  | 0
G244.2 | Width: 0.4-1.22m; to sides of the ring beam and false slab | m² | 7.3 |  | 0
Reinforcement
Deformed High Yield Steel Bars
High yield square twisted or ribbed bars to BS4449 and of the following sizes
G525 | Nominal size, 6 - 16mm | kg | 106
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
G564 | Nominal mass 4-5 kg/m² | m2 | 17.1
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
G811 | Class U2 wood float finish to top of floor of Pump Stations | m2 | 12.26 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK - FITTINGS AND VALVES
Iron or Steel pipe fittings to BS 534; all Epoxy coated Steel pipe; PN 16 flanges to BS 4504; not in trenches including casting in as required
Bends
J311.1 | DN 63mm x 45deg flanged small radius bend | No | 2 |  | 0
J311.2 | DN 63mm x 90deg flanged small radius bend | No | 2 |  | 0
Junctions and Branches
J312.1 | DN 63mm flanged tee | No | 2 |  | 0
Tapers
All flanged taper to BS 4772, flanges to BS 4504 all to PN16, and of the following sizes
J331 | 90/63 mm ND | nr | 1 |  | 0
Adaptors
Flanged adaptor to fit GI pipe spigots to BS 3505, flanges to BS 4505, all to PN16, and of the following sizes
J351.1 | 63 mm ND | nr | 1 |  | 0
Straight specials - DN 90mm pipe with fittings
J381.1 | Stainless Steel - SS 304 riser pipes DN 80mm PN16 from submersible pump to pumphouse; complete to match pump outlet size and pumphouse pipe work | m | 39 |  | 0
Gate Valves
All flanged gate valve installation to BS 5153, flanges to BS 4505, all to PN 16 complete inclusive of hand wheel and all fittings, as shown in the drawing for the following sizes
J811.1 | DN 63 mm | No | 2 |  | 0
Air Valves
Flanged VENT-O-MAT CI small orifice anti-shock double air relief valve as specified, flanges to ISO 2441, complete with isolating flanged gate valve to BS 5150 all to PN 16 for the following pipe sizes
J861.1 | DN 40mm | No | 1 | 0 | 0
Washout
J861.2 | Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, uPVC down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN16 | No | 1 |  | 0
Pressure Gauge
J891.1 | BH10 - WIKA pressure gauge, DN 50mm case, glycerine filled with 15mm male thread | No | 1 |  | 0
Non-Return Valves
All flanged non-return valve installation to BS 5153, flanges to BS 4505, all to PN 16 complete inclusive of all fittings, as shown in the drawing for the following sizes
J861.1 | DN 65mm | No | 1 |  | 0
Bulk Flow Meter
J991.1 | Flanged DN 65mm MEINECKE Cosmos WP bulk water meter | No | 1 |  | 0
|  |  |  | Carried to Collection | 0
BRICKWORK & MASONRY
Dense concrete brickwork to BS 7263, jointed with ordinary 1:5 cement mortar, hoop irons every three courses, including 1:4 cement plaster to both faces complete with concrete louvres, as detailed in the drawings, for walls of the following thickness
U521 | 230 mm thick | m2 | 105.1
|  |  |  | Carried to Collection | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
V321 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 6.1 |  | 0
Masonry
External quality weather guard paint, two coats, to the following smooth concrete surfaces; include surface preparation and under coat as specified
V363 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 39 |  | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
V563 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m2 | 69 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
W421.1 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 25 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
W421.2 | 200 mm thick | m | 22 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
W441 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 39.4 |  | 0
Rendering- Rough Cast
W511 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m2 | 47.3 |  | 0
Rendering- Mortar
W153 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary cement mortar | m2 | 56.14
|  |  |  | Carried to Collection | 0
MISCELLANEOUS WORKS
Roofing
K-B-W-1.1 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, facia board and all roofing timber, eave closing, gauge 26 prepainted GCI resin sheeting and ridges | m² | 41.72 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories
M W-1.2 | Double leaf door overall size 1800 x 2100mm high filled in with 20 x 2mm thick mild steel square hollow section grating welded to door, complete | nr | 1
Windows
M W-1.3 | 1200*1500mm Pompei Grill, with burglar proof as per the drawings and/or as per Engineer's istructions.Rate should cater for painting of windows and doors surfaces with both protective and finishing layers of paint to Engineer's satisfaction | Nr | 2
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page M-W-2 |  |  |  | 0
| Collection, Page M-W-3 |  |  |  | 0
| Collection, Page M-W-4 |  |  |  | 0
| Collection, Page M-W-5 |  |  |  | 0
| Collection, Page M-W-6 |  |  |  | 0
| Collection, Page M-W-7 |  |  |  | 0
| Collection, Page M-W-8 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## M-W-3-PM
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-W-3
DESCRIPTION: | MUWAYO PUMPING MAINS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | ha | 0.1936 |  | 0
Trees
Cut and dispose of trees of the following girth; include removal of stump and backfilling the hole left with top soil
D210 | Girth 500 mm-1 m | nr | 10 |  | 0
Stumps
Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
D310 | Diameter 150-500 mm | nr | 5 |  | 0
Excavation in pipe trenches, laying and backfilling as detailed in the tech. specs; in the following materials
L111.1 | Allowing for extra Over; In rock excavation | m³ | 36 |  | 0
Laying of Pipes
Plastic Pressure Pipes
uPVC pressure pipes to BS3505, with flexible joints to BS4346 all to PN16, OD90mm, laid in trench and backfilled as detailed in the tech. specs; to the following depths
I513.1 | Depth not exceeding 2.0 m | m | 1640 |  | 0
Ductile Iron Pressure Pipes
Ductile Iron pressure pipes to BS3505, BS4346 , DN 80mm,
I311 | Not in trenches (Anchored on rocks) | m | 800 |  | 0
PIPEWORK-FITTINGS AND VALVES
uPVC Pipe Fittings external epoxy coated to AWWA C213
Adaptors
Flanged adaptor to fit uPVC pipe spigots to BS 3505, flanges to BS 4505, all to PN16, and of the following sizes
J351.1 | 90 mm ND | nr | 3 |  | 0
Bends
uPVC all flanged 90 degree bend, to BS 4772, flanges to BS 4504, all to PN16, cement mortar lined, and of the following sizes
J311.1 | 90 mm ND | nr | 3 | 0 | 0
GI all flanged ND90mm duckfoot bend, to BS 4772, flanges to BS 4504, all to PN16, cement mortar lined, and of the following angles
J311.4 | 90 deg | nr | 1 | 0 | 0
J311.5 | 45 deg | nr | 2
|  |  |  | Carried to Collection | 0
Valves and Penstocks
Gate Valves: Hand Operated
All flanged CI gate valves to BS 5150, flanges to BS 4505, all to PN 16 for operation by tee key, with cap and extension spindle not exceeding 1.5 metres long, and of the following sizes
J811.1 | 90 mm ND | nr | 3 |  | 0
Air Valves
Flanged anti shock, anti surge double air valve, 113 mm ND, as specified, flanges to ISO 2441, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN 16, as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 90 mm ND | nr | 2 |  | 0
Washouts
Type 2 Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, uPVC down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN16
J911.1 | 90 mm ND | nr | 1 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 1 |  | 0
Pre-cast Concrete Chambers
Concrete air valve chamber, complete as specified in the drawings, and of the following depths
K251.1 | Depth not exceeding 1.5m | nr | 2 |  | 0
Valve Surface Boxes
Valve surface box for DN 50 - 100 valves, with lockable cover securely attached to main body of surface box by chain or bolt, include down pipe, complete as specified and to the following depths
K251.2 | Depth not exceeding 1.5m | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Crossings
Open Channels
Stone pitched or concrete lined open channel crossings for pipes of the following sizes
K681 | Not exceeding 300 mm ND | nr | 2 |  | 0
Unlined open channel crossings for pipes of the following sizes
K682 | Not exceeding 300 mm ND | nr | 2 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.2 | Diameter not exceeding 300 mm ND | m | 50 |  | 0
Other Pipework Ancillaries
Marker Posts-Concrete with galvanized alumnium plates
K820.1 | Marker posts for gate valves | nr | 2 |  | 0
K820.2 | Marker posts for air valves | nr | 1 |  | 0
K820.3 | Marker posts for wash outs | nr | 1 |  | 0
K820.4 | Marker posts for pipes @ 200m spacing | nr | 12.2 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 7.38 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731.1 | Diameter not exceeding 300 mm ND | nr | 5 |  | 0
0
0
L731.2 | Allow for construction of reinforced concrete supports with M24 steel G8 bolts to support pipes on hard ground to Engineer's approval | m³ | 6.6667 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 500 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 50 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 50 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page M-W-3/1 |  |  |  | 0
| Collection, Page M-W-3/2 |  |  |  | 0
| Collection, Page M-W-3/3 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## M-W-6-DN
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M- W-6
DESCRIPTION: | MUWAYO DISTRIBUTION NETWORK
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D110 | General site clearance for pipe trench | ha | 1.373 |  | 0
Ductile Iron Pressure Pipes
Ductile Iron pressure pipes to BS3505, BS4346 , DN 100mm,
I311 | Not in trenches (Anchored on rocks) | m | 800 |  | 0
Plastic Pipes
Plastic Pressure Pipes
uPVC pressure pipes to BS3505, with flexible joints to BS4346 all to PN16, OD75mm, laid in trench and backfilled as detailed in the tech. specs; to the following depths
I513.1 | Depth not exceeding 2.0 m | m | 0 |  | 0
HDPE pressure pipes to BS3505, with flexible joints to BS4346 all to PN10, OD 90mm, laid in trench with all necessary fittings and, backfilled as detailed in the tech. specs; to the following depths
I712.1 | Depth not exceeding 2 m | m | 800 |  | 0
HDPE pressure pipes to BS3505, with flexible joints to BS4346 all to PN10, OD63 mm, laid in trench with all necessary fittings and, backfilled as detailed in the tech. specs; to the following depths
I712.2 | Depth not exceeding 2 m | m | 1950 |  | 0
HDPE pressure pipes to BS3505, with flexible joints to BS4346 all to PN10, OD 50mm, laid in trench with all necessary fittings and,backfilled as detailed in the tech. specs; to the following depths
I712.1 | Depth not exceeding 2 m | m | 5531 |  | 0
HDPE pressure pipes to BS3505, with flexible joints to BS4346 all to PN10, OD 40mm, laid in trench with all necessary fittings and, backfilled as detailed in the tech. specs; to the following depths
I712.1 | Depth not exceeding 2 m | m | 2815 |  | 0
Excavation in pipe trenches in the following materials
L111.1 | Extra Over; In rock | m³ | 255.3075 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Junctions and Branches
All flanged GI tee to BS 4346, flanges to BS 4504 ,all to PN16 and of the following sizes
J521.1 | ND110mm | nr | 3 |  | 0
J521.2 | ND75mm | nr | 2
J521.3 | ND50mm | nr | 1
All flanged concentric taper to BS4772, flanges to BS4504 all to PN10, cement mortar lined, and of the following sizes
J331.1 | ND110x50 | nr | 1
J331.2 | ND110x32 | nr | 1
J331.3 | ND110x75 | nr | 2
J331.4 | ND50x40 | nr | 2
J331.5 | ND75x50 | nr | 1
J331.6 | ND75X40 | nr | 4
Flanged Adaptor to fit PE pipes to ISO 4427 Spigot
J451.1 | OD90mm | nr | 4
J451.2 | OD63mm | nr | 3
J451.3 | OD40mm | nr | 1
J451.4 | OD50mm | nr | 4
CI compression Adapter
| ND110mm |  | 1
All HDPE flanged tee to BS 4346, flanges to BS 4504 ,all to PN16 and of the following sizes
J621.3 | 63/50 mm ND | nr | 0 |  | 0
Bends
HDPE bends with push-fit joint for use with HDPE pipes, to ISO 2531, all to PN 16, and of the following sizes
J612.1 | 90 mm OD all socketed 900 bend | nr | 2 |  | 0
J612.2 | 50 mm OD all socketed 900 bend | nr | 1 |  | 0
End caps
Compression HDPE end caps to fit HDPE spigots, to ISO 161 and to PN 16 of the following spigot sizes
J691.1 | 90 mm OD | nr | 1 |  | 0
J691.2 | 63mmOD | nr | 1
J691.3 | 50 mm OD | nr | 4 |  | 0
J691.4 | 40mm OD | nr | 3
J691.5 | 32mm OD | nr | 15
Gate Valves: Hand Operated
All flanged CI gate valves to BS 5150, flanges to BS 4505, all to PN 16 for operation by tee key, with extension spindle not exceeding 1.5 metres long, and of the following sizes
J811.1 | 90 mm ND | nr | 2 |  | 0
J811.2 | 50 mm ND | nr | 6 |  | 0
Air Valves
Flanged anti shock, anti surge double air valve, 40 mm ND, as specified, flanges to ISO 2441, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN 16, as specified and all fittings necessary to make the connection complete; for the following pipe sizes
J862.1 | 90 mm ND | nr | 1 |  | 0
J862.2 | 50 mm ND | nr | 2 |  | 0
|  |  |  | Carried to Collection | 0
Washouts
Type 1 Washout as specified in the drawings, complete with tee, adaptors, drainage pipes, gate valve, flap valve, thrust blocks, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN16
J912.1 | 90 mm ND | nr | 1 |  | 0
J911.2 | 50 mm ND | nr | 2 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Other Chambers
In-situ Concrete Chambers
Concrete washout outfall structure, complete, as specified in drawings, and of the following depths
K231 | Depth not exceeding 1.5m | nr | 3 |  | 0
Pressure release valve
K232 | Supply, install, and commission a complete central pressure-reducing valve (PRV) assembly on mainline pipeline, comprising: One (1) pilot-operated pressure-reducing valve, DN80 (3") or DN100 (4") (e.g., Cla-Val 90-01, Singer PR-160, BERMAD 720 or approved equivalent), rated for inlet pressure up to 6 bar and adjustable outlet pressure 1.5–3 bars;.Two (2) isolation valves (inlet and outlet), resilient-seated, same diameter as PRV;One (1) bypass line with manual gate/globe valve; Two (2) pressure gauges, glycerin-filled, 100 mm dial, range 0–10 bar (inlet and outlet),All associated fittings (flanges, reducers, couplings); Concrete valve chamber or MANHOLE with lockable cover and drain provision;Piping supports and base slab;Testing, pressure setting, and commissioning All to be done according to the drawings and specifications, complete in all respects. | nr | 1
Manholes
Construct a 1x1m manhole using Hard burnt clay bricks to BS 3921(3.5N/mm² compressive strength) bedded and jointed in cement and sand(1:3) mortar, including 1:4 cement plaster to both faces complete, covered with a reinforced concrete slab, including all earthwork, building work and concrete works, as protection to below ground installation. Rate to include the cost of installation of asleeve pipe at wall crossing.
K251.2 | Depth not exceeding 1.5m | nr | 15 |  | 0
Crossings
K684 | Anchor blocks for UPVC Pressure pipes OD 110mm PN10 | nr | 5 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of gravel roads for the following pipe sizes (Inclusive of processing the necessary approvals from the relevant authorities)
K731.2 | Diameter not exceeding 300 mm ND | m | 50 |  | 0
Other Pipework Ancillaries
Marker Posts
K820.1 | Marker posts for gate valves | nr | 10 |  | 0
K820.3 | Marker posts for wash outs | nr | 3 |  | 0
K820.4 | Marker posts for pipes @ 200M spacing | nr | 58.5 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 99.864 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
L731 | Diameter not exceeding 300 mm ND | nr | 5 |  | 0
Surrounds
Pipe surrounds of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 100 |  | 0
Pipe surrounds of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 100 |  | 0
Pipe surrounds of mass concrete, and for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 50 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page M-W-6/1 |  |  |  | 0
| Collection, Page M-W-6/2 |  |  |  | 0
| Collection, Page M-W-6/3 |  |  |  | 0
| Collection, Page M-W-6/4 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## M-W-7-IN
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-W-7
DESCRIPTION: | INTENSIFICATION NETWORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
D100 | General site clearance for pipe route | m2 | 7350 |  | 0
PIPEWORK-PIPES
Allow for Plastic Pressure Pipes- Distribution
HDPE pressure pipes to BS 3505, include unions / sockets, all to PN 16, OD 40 mm, laid in trench to the following depths
I711.1 | Depth not exceeding 1.5m | m | 4900 |  | 0
HDPE pressure pipes to BS 3505, include unions / sockets, all to PN 16, OD 32 mm, laid in trench to the following depths
I711.2 | Depth not exceeding 1.5m | m | 500 |  | 0
HDPE pressure pipes to BS 3505, include unions / sockets, all to PN 16, OD 25 mm, laid in trench to the following depths
I711.3 | Depth not exceeding 1.5m | m | 0 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Make a connection for OD 40 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 40 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN16
J791.1 | OD 63mm | nr | 0 |  | 0
J791.2 | OD 50mm | nr | 0 |  | 0
Make a connection for OD32HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 32 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN16
J791.1 | OD 90mm | nr | 1 |  | 0
J791.2 | OD 63mm | nr | 5
J791.3 | OD 50mm | nr | 4
J791.4 | OD 40mm | nr | 5 |  | 0
Make a connection for OD25HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (A DN 25 branched Tee with body sizes as below, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of HDPE pipes for the following main sizes and maximum pressure rating of PN16
J791.1 | OD 63mm | nr | 0 |  | 0
J791.2 | OD 50mm | nr | 0 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
MANHOLES
L999.1 | Construct a 1x1m manhole using Hard burnt clay bricks to BS 3921(3.5N/mm² compressive strength) bedded and jointed in cement and sand(1:3) mortar, including 1:4 cement plaster to both faces complete, covered with a reinforced concrete slab, including all earthwork, building work, concrete works, plumbing, all relevant fitings all to 32mmOD; brass stop cock, domestic water meter, all to PN 10 and pipe sleeves at wall crossing. The pipe outlet must be plugged awaiting connection to a prepaid meter system. | nr | 15
Crossings
Open Channels
Unlined open channels crossings for pipes of the following sizes
K681 | Not exceeding 300 mm ND | nr | 4 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of murram roads for the following pipe sizes
K731 | Not exceeding 300 mm ND | m | 20 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
L111 | In rock | m³ | 132.3 |  | 0
Surrounds
Pipe surrounds, of selected excavated granular material, for the following pipe sizes
L521 | Diameter not exceeding 200 mm ND | m | 100 |  | 0
Pipe surrounds, of imported granular material, for the following pipe sizes
L531 | Diameter not exceeding 200 mm ND | m | 50 |  | 0
Pipe surrounds, of mass concrete , for the following pipe sizes
L541 | Diameter not exceeding 200 mm ND | m | 20 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page M-W-7/1 |  |  |  | 0
| Collection, Page M-W-7/2 |  |  |  | 0
| Collection, Page M-W-7/3 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## M-W-8-CC
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-W-8
DESCRIPTION: | CONSUMER CONNECTIONS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Public Stand Posts
Construct a three faucet Stand Post complete as in drawing including all earthwork, building work, concrete works, plumbing, drains and soak pit, all relevant fittings; galvanized iron pipe and fittings, brass stop cock, lockable steel meter protection box, taps and domestic water meter, raising meter above ground, GI/HDPE connection, all to PN 16 (service line measured separately under items I712)
K-K-W-10.1 | ND 20 mm (3/4") | nr | 15 |  | Rate only
Private Promotional Connections
K-K-W-10.2 | Allow for promotional connections,30m OD 12mm pipe from the service line, with all the pipe fittings including a water meter, lockable steem meter protection box, among others all to PN 16 | nr | 0 |  | Rate only
Note:
All fittings are to be approved by the Engineer.
Carried to Summary |  |  |  |  | 0

## M-W-9-M&E
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-W-9
DESCRIPTION: | MECHANICAL & ELECTRICAL WORKS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
MECHANICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
ME 1.1 | Borehole Pumps
ME 1.1.1 | Electric multistage centrifigual submersible borehole pumpset, preferable Lorentz pump as PSk3-15 C-SJ17-18 , Rp 6" Pumpset Q = 13/hr(Max.), H = 133m (Actual/Max.) total head, with controller PSk3-7, Max. power of 8.3 kW, input Voltage of max. 850 V with a high efficiency 3-phase AC Drive Brushless Motor; Model Lorentz Motor AC DRIVE SUB 6" 11kW, rated Power 8.3kW and 50m of 4 mm² 3-phase cable for power and 1-phase cable for ground. (ref the PV Simulation report attached) | No. | 1 |  | 0
ME 1.1.2 | Surge protectors2 (See details in PV & Pump sizing report attached) | nr | 1
ME 1.1.3 | Well Probe V2 ( see details in PV & Pump Sizing report attached) | nr | 1
ME 1.1.4 | Make provisions, supply and install a Liquid Pressure sensor, LSP - 1000, Pressure gauge 0 to 10bars Installed along the rising main.( see details in PV & Pump Sizing report attached) | nr | 1
ME 1.1.5 | Make provisions, supply and install a pressure switch: 1 to 5 bar, in the water storage tank. ( see details in PV & Pump Sizing report attached) | nr | 0 |  | Rate only
ME 1.1.6 | Assortment of electrical cables, interconnects, concrete nails & screws and accessories for complete system wiring, including where necessary, underground cables, wired in full conduit technique; supplied and installed to specifications. | sum | 1
ME 1.1.7 | PV Disconnect 400-50- 3 - S box connection with DC Disconnect Switch and Lightning surge protection with maximum voltage of 1000V and maximum current of 50A, See details in PV and Pump Sizing report | nr | 1
ME 1.1.8 | Motor cable (water resistent Cable), 6 mm² | m | 0 |  | Rate only
ME 1.2 | Manufacturer's recommended spares for 3 years operation of pump | set | 1 |  | Rate only
ME 1.2 | Solar Modules |  |  |  | 0
| Supply and installation of 330W norminal panel rating Solar Panels(Modules) 21.4KW nominal array rating, 11kW power rating, including metallic support frame, cables, HDPE drop pipes, cover plates, clips, earthing protection, all accessories complete to Engineer's approval for the borehole pumping system and lighting for the pumphouse | Wp | 20000 |  | Rate only
0
ME 1.2.1 | 11kW AC/DC Inverter and AC motor controller with 3phase x 415v output at 98% efficiency with hybrid capability of DC solar AC input. Input voltage upto 850vdc, 415VAC-variable speed drive with MPPT technology, 50Hz (Variable speed, +5hz selectable speed increase), with surge protection, overload, underload, pump dry-run and full-tank shutoff protection; shall be non-programmable by human-operator. Enclosure class: IP65 with no access for rodents,insects or lizards. | No | 1 |  | Rate only
|  |  |  | Carried to Collection | 0
ME 1.3 | Inline Doser
ME 1.3.1 | Supply and Install the KLORMAN inline chlorination Equipment approved by the Engineer including all inlet, outlet, drain, venturi, overflow and interconnection connection pipes to solution tank (PVC, 1") with valves and all accessories with a minimum capacity of 10-60m3/hr | nr | 1 |  | 0
ME 1.3.2 | Construct a 200mm thick meter chamber, 1500x1000mm using concrete blocks to protect the chlorination equipment, with a precast reinforced concrete cover raising above the ground level by 300mm including all earthwork, placing of concrete works. Provide a 110mmOD PVC pipe as top sleeve to protect the pipes at wall crossing with the chamber. The chamber cover should be finished smooth. | nr | 0 |  | 0
0
|  |  |  | Carried to Collection | 0
ELECTRICAL WORKS
Supply and complete installation of all items as specified and as directed by the Engineer
Borehole Pump House
EE 1.1 | Lighting and Small Power
EE 1.1.1 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 5 |  | 0
EE 1.1.2 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes. | No | 3 |  | 0
0
EE 1.1.3 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 3 |  | 0
EE 1.1.4 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 3 |  | 0
0
EE 1.1.5 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 1 |  | 0
EE 1.1.6 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 3 |  | 0
0
EE 1.1.7 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 3 |  | 0
|  |  |  | 0 | 0
EE 1.1.8 | High quality 800W Electronic inverter rated at 12V, input voltage, output voltage 240V, complete with charge controler 50-80Amps; installation to the approval of the supervising Engineer | Item | 1 |  | 0
0
EE 1.1.9 | Supply and install mounted on the roof, 2 solar pannels each of 150W, 12v | Item | 1 |  | Rate only
0
EE 1.1.10 | Supply and install solar batteries each of 100mAhr of 12V, well mounted on a stand raised 30cm above the floor, in the pump House | No | 2 |  | Rate only
EE 2 | Earthing and Lightning Protection |  |  | 0
EE 2.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 10 |  | 0
0
EE 2.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 6 |  | 0
0
EE 2.3 | Test clamp complete as by FURSE or equal. | No. | 6 |  | 0
0
EE 2.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 6 |  | 0
EE 2.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories. | M | 20 |  | 0
EE 2.6 | 100KVA Electronic stabilizer rated at 400V, 50Hz 3 phase, input voltage +/-25%, output voltage +/-5%, complete with independent phase control, input/output isolators and bypass switch and all accessories as made by Orteo of Italy or equal approved. | No. | 1 |  | Rate only
EE 2.7 | Motor Control Centre for boreholes incorporating main circuit breaker, starter, controls and protection for pump (HIGH/LOW pressure and dry running), under and overvoltage relay and single phasing relay, power monitor, hour, volt and Amp meters, and all accessories complete as in specifications | No. | 1 |  | Rate only
|  |  |  | Carried to Collection | 0
0
EE 2.8 | Armoured cable 4corex10mm2 PVC/SWA/PVC laid in conduits from pump control panels to pumps complete | m | 100 |  | 0
EE 3 | Water Office and guard house
EE 3.1 | Lighting and Small Power
EE 3.2 | Lighting points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge PVC conduit surface/concealed conduit with drops concealed in walls to switch positions complete with MK steel boxes complete with all accessories. | No | 4 |  | 0
EE 3.3 | Socket outlet points wired by 3 x 2.5mm2 SC PVC copper cables in 25mm heavy gauge steel surface conduit complete with all accessories including boxes; installed at water office and guard house. | No | 2 |  | 0
EE 3.4 | Cast aluminium waterproof bulkhead with 70W HPS lamp and polycarbonate bowl retained by tamper resistant fixings to IP44 as Pierlite or equal approved (Light Type S) | No. | 3 |  | 0
EE 3.5 | T5 1x28W,1200mm, surface fluorescent luminaire for 28W T5 linear fluorescent lamps weather proof and corrosion resistant, with electronic control gear, as PIERLITE 1x28W T5 or equal approved. (Light Type F1) | No. | 3 |  | 0
EE 3.6 | 100A 4 way TPN MCCB wall mounted recessed Distribution Board, complete with integral isolator, MCCBs, RCCBs, and all accessories, as L & T or equal approved. | No | 3 |  | 0
0
EE 3.7 | 13A 2gang 3pin metal clad switched socket outlets complete with all accessories. | No | 3 |  | 0
EE 3.8 | 6A 2gang metal clad wall switch for lights complete with all accessories. | No | 6 |  | 0
0
EE 3.9 | High quality 800W Electronic inverter rated at 12V, input voltage, output voltage 240V, complete with charge controler 50-80Amps; installation to the approval of the supervising Engineer | Item | 2 |  | 0
EE 3.10 | Supply and install, 2 solar pannels each of 150W, 12v, mounted and secured on the roof top. | Item | 2 |  | 0
EE 3.11 | Supply and install solar batteries each of 100mAhr of 12V, well mounted on a stan raised 30cm above the floor, in the pump House | Item | 4 |  | 0
EE 4.0 | Earthing and Lightning Protection
EE 4.1 | Copper tape of hard drawn high conductivity copper 3mm x 25mm cross section for horizontal and down conductors complete with fixing clips and all accessories as by FURSE or equal. | M | 4 |  | 0
EE 4.2 | Air terminals 20x1200mm complete with tape adapters, spikes and all accessories by FURSE or equal. | No. | 1 |  | 0
EE 4.3 | Test clamp complete as by FURSE or equal. | No. | 1 |  | 0
EE 4.4 | Earth Electrodes 20x1200mm made from hard drawn copper or copper weld complete with cap, earth clamp, manhole and all accessories as made by FURSE or equal. | No. | 1 |  | 0
EE 4.5 | General Earthing by 70mm2 stranded bare copper cable complete with all accessories and earthing marterial to quantites approved by the supervising Engineer. | m | 5 |  | 0
EE 4.6 | 63A TPN IP65 Isolator. | No. | 2 |  | Rate only
EE 4.7 | 100A TPN IP65 Isolator. | No. | 2 |  | Rate only
EE 5.0 | Power Supply to Water Office
EE 5.1 | Allow a Provisional Sum for Utility connection from nearby UMEME supply to distribution boards | Item | 1 |  | Rate only
EE 5.2 | Allow for profit and overheads on above. | % |  |  | Rate only
EE 5.3 | Lockable Meter Box to UMEME approval (400x600x200mm) in 2mm MS Sheets complete with cutouts and all accessories | No. | 1 |  | Rate only
|  |  |  | Carried to Collection | 0
| Power Supply |  |  | 0
0
EE 6.0 | Electrical Power Supply
EE 6.1 | Transformer & 11KV Switchgear
EE 6.2 | 500KVA, 3phase, 11KV/433V Dyn11, 50Hz oil filled indoor, ground mounted transformer, conservator tank with silica gel breather, Temperature gauge, off-load tap changer, explosion vent, and additional neutral for grounding, and all accessories all to comply with UMEME Standards. | No | 1 |  | Rate only
EE 6.3 | Allow a Provisional Sum for Utility connections at 50KV and metering unit. | Item | 1 |  | Rate only
| Solar Power Unit |  |  | 0
1.Lorentz PV as LC325-P72 High-efficiency PV, Polycrystalline or monocrystalline solar panels, @325Wp, 8.84Imp, 37.3 Vmp, See details in PV and Pump Sizing Report attached OR 2. Soleil power solar panels monocrystalline or Polycrystalline of Module of similar wattage.
EE 6.4 |  | nr | 40 |  | 0
0
EE 6.6 | PV Protect 1000-125 Surge protective device for PV systems with maximum voltage of 1000V and maximum current of 125A, See details in PV and Pump Sizing report | nr | 1 |  | 0
Solar PV Mounting Structure
EE 6.7 | Solar Array mounting frame made from galvanised rust-free/resistant steel metal supported by galvanised steel pipes/angle sections onto a reinforced concrete base constructed to specifications. Special bolts and nuts with arren-keys shall be supplied for fastening modules, enhanced for theft-proof or spot welded, earthing protection, all accessories complete to Engineer's approval - inclusive of casting of concrete pads - Ref drawing attached. | item | 1 |  | 0
Water Monitoring system
EE 6.8 | Lorentz Bulk Meter, WP Water meter DN50mm, See details in the PV & Pump Sizing report attached. | nr | 1 |  | 0
EE 6.9 | PS Communicator 3G, Lorentz | nr | 1 |  | 0
EE 6.10 | Solar Pannel LC 20Wp, Lorentz | nr | 1 |  | 0
EE 6.11 | 12V AGM Lead acid Battery, Min Capacity 5Ah(Lorentz) | nr | 1 |  | 0
EE 6.12 | Liquid Level Sensor (0-60m) | nr | 1 |  | 0
EE 6.13 | Subscription 1/5 years | nr | 1 |  | 0
EE 6.14 | Weld and fix as directed in the drawings, 1000x700mm metal casement out of 1.5mm thick GMS plate painted in three layers to the satisfaction of the supervising Engineer, to house the PS communicator, PV disconnect, Controller and PV Protect. | item | 1 |  | 0
EE 6.15 | Supply and install metallic support frame, cables, HDPE drop pipes, cover plates, clips, earthing protection, all accessories complete to Engineer's approval | No. | 1 |  | 0
|  |  |  | Carried to Collection | 0
Solar Invertor
EE 6.16 | A 50kVA/360V star online solar PCU solar inverter with multiple point trackers, a wide input voltage range, an integrated data logger as well as RS485/Wi-Fi interface. Model: UTL 50GT, with Max. DC power; 65kW, 1000V Max DC Voltage/Nominal DC voltage, 3No. MPP Trackers with 4 strings each, 36A Max. input currrent per MPP tracker, 50kW Nominal AC Output Power | No. | 1 |  | Rate only
Hydroelectricity
| Lighting system, overhead 3-phase powerline extension, lightening protection, etc. and preparation of general arrangement schematics and wiring diagrams for the pump controls and instrumentation panel, cable schedule instrument loop diagrams and cable termination schedules for the approval of the Engineer | sum | 1 |  | Rate only
| Supply, installation, testing and commissioning of overhead medium voltage 33kV power line from existing UMEME power line to the pump house inclusive of supply, installation, testing and commissioning of an appropriate transformer | km | 1 |  | Rate only
| Allow for profits and overheads on Item No.EE 1.3.5 & ME 1.3.6 | % | 0 |  | Rate only
EE 6.17 | Supply and install Solar powered Lighting system complete, with light unit on 6m-GI poles to the approval of the Engineer (at the intake and reservior). | No. | 2
SB 1.0 | Permanent Signboard for visibility
SB 1.1 | Design, fabricate, deliver and install the permanent project visibility signboard at locations identified by the client at both the reservior and intake stations. The information on the board to be provided by the client and all implementation of technical work as per the drawings. | Item | 2 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page M-W-9/1 |  |  |  | 0
| Collection, Page M-W-9/2 |  |  |  | 0
| Collection, Page M-W-9/3 |  |  |  | 0
| Collection, Page M-W-9/4 |  |  |  | 0
| Collection, Page M-W-9/5 |  |  |  | 0
| Collection, Page M-W-9/6 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## M-W-10
GOAL-UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | M-W-10
DESCRIPTION: GUARD AND PUMP ATTENDANT HOUSE
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
General Site Clearance
M.W.1 | General site clearance | m2 | 49.5618 |  | 0
EARTHWORKS
Excavation for foundations
Topsoil
M.W.2 | Strip site of top soil average depth 150mm and deposit in heaps at an appropriate place 300m away from site | m3 | 7.4343 |  | 0
Ordinary Soil
Excavation for foundations in all materials including rock or artificial hard material, commencing surface is the stripped ground level and deposit in heaps at an appropriate place 300m away from site
M.W.3 | Depth for Buildings 0-1.5m | m3 | 25.4765 |  | 0
Excavation Ancillaries
M.W.4 | Allow for all excavation ancillaries including trimming, preparation, and compaction of excavated surfaces, disposal of excavated material, and timber supports to all excavated surfaces | Sum | 1 |  | 0
Anti-termite Treatment
M.W.5 | Apply approved anti-termite treatment to surfaces of hardcore blinding, sides and bottoms of foundation excavations to the manufacturer's instructions | sum | 1 |  | 0
Filling
Filling to structures by methods specified and to depths as shown in the drawings with the following materials
M.W.6 | Selected imported granular material other than topsoil, rock or artificial hard material to building area and compacted to 98% MOD AASHTO | m³ | 14.4681 |  | 0
M.W.7 | 50mm thick bed of approved imported sand blinding on top of hardcore fill well spread, levelled, rammed and consolidated to the Engineer's satisfaction | m³ | 0.73469 |  | 0
M.W.8 | 200mm thick bed of approved imported hardcore well spread, levelled, rammed and consolidated on stabilized ground to the Engineer's satisfaction | m³ | 2.9388 |  | 0
|  |  |  | Carried to Collection | 0
IN-SITU CONCRETE
Provision of Concrete
Ordinary Designed Mix Concrete
Grade C20
Designed mix, grade C20 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
M.W.9 | 10mm aggregate | m³ | 0 |  | Rate only
Grade C25
Designed mix, grade C25 concrete, to BS 5328, with ordinary portland cement to BS 12, aggregate to BS882, for the following aggregate sizes
M.W.10 | 10mm aggregate | m³ | 0 |  | Rate only
Placing Mass Concrete
Bases, Footings and Ground Slabs
Placing mass concrete, for strip foundations, grade C30, of the following thickness
M.W.11 | Thickness 200mm | m³ | 3.7743 |  | 0
Placing Reinforced Concrete
Bases, Footings and Ground Slabs
Placing reinforced concrete grade C25, for floor slab and steps of the following thickness
M.W.12 | To oversite slabs of thickness 100mm | m³ | 2.0793 |  | 0
| To Suspended slab of thickness 150mm |  | 0.68502 |  | 0
| To Stair case | m³ | 0.9435 |  | 0
| To Suspended slab of thickness 100mm for the waterborne toilet | m³ | 0.9 |  | 0
Beams
Placing reinforced concrete, grade C25, for ring beam of the following cross-sectional area
M.W.13 | Cross-sectional area 0.03 - 0.1 m2 | m³ | 1.42 |  | 0
CONCRETE ANCILLARIES
Formwork-Fair Finish
Fair Finish Plane Horizontal
Plane fair finish horizontal formwork of the following width
M.W.14 | Width: 0.4-1.22m | m² | 2.85 |  | 0
Fair Finish Plane Vertical
Plane fair finish vertical formwork of the following width
M.W.15 | Width: 0.4-1.22m; to sides of the ring beam | m² | 10.4 |  | 0
|  |  |  | Carried to Collection | 0
Reinforcement
Deformed High Yield Steel Bars
High yield ribbed bars to BS4449 and of the following sizes
M.W.16 | 12mm bars at 200mm spacing c/c to 150mm thick suspended slab - allow for binding of rebars / slab | kg | 158 |  | 0
Steel Fabric
High tensile steel fabric reinforcement to BS 4483, fabric reference A252, cast in concrete slab with minimum 200mm end side laps, and of the following mass
M.W.17 | Nominal mass 4-5 kg/m² | m2 | 34.5 |  | 0
Concrete Accessories
Finishing of Top Surfaces
Finishing of top surfaces by the following methods
M.W.18 | Class U2 wood float finish to top of the 02 slabs | m2 | 34.5 |  | 0
BRICKWORK, BLOCKWORK, AND MASONRY
Foundation Plinth Wall
Hard Burnt clay bricks to BS3921 (3.5N/mm² Compressive strength) bedded and jointed in 1:3 Cement Sand mortar mix.
| 230mm thick | m2 | 39.7 |  | 0
0
| Superstructural walls |  |  |  | 0
0
| Hard Burnt clay bricks to BS3921 (3.5N/mm² Compressive strength) bedded and jointed with ordinary 1:4 cement mortar, hoop irons every three courses, for walls of the following thickness |  |  |  | 0
| 230mm thick wall | m2 | 39.33 |  | 0
| 150mm think wall | m2 | 24.24 |  | 0
WATER PROOFING
Protective Layers
Flexible Sheeting
Flexible polyethylene sheeting, gauge 1000, or similar approved, laid with 300mm overlaps at joints, to the surface of sand blinded hardcore fill
M.W.19 | Surfaces of blinding hardcore inclined at an angle not exceeding 30 degrees to the horizontal | m² | 28.2 |  | 0
Damp proof course of Hessian based bitumen impregnated fabric to BS 6398 bedded on 1:4 cement and sand mortar with 150mm overlaps at joints; for the following wall
M.W.20 | 150 - 230 mm thick | m | 26 |  | 0
Sand and Cement Screed
Sand and cement screed of 1:3 cement sand mortar, applied to concrete floors, 25 mm thick, prepared and applied as specified, and finished with a steel float
M.W.21 | Surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 22.216 |  | 0
| Ditto but dwarf walls to sofit of suspended 02 slabs and extending to support steel solar heater. | m2 | 12 |  | 0
Rendering- Rough Cast
M.W.22 | Apply rough cast to external wall surfaces inclined at an angle exceeding 60 degrees to the horizontal in 1:3 ordinary cement mortar to the Engineer's satisfaction | m² | 39.3 |  | 0
Rendering- Mortar
M.W.23 | Surfaces to internal walls inclined at an angle exceeding 60 degrees to the horizontal in ordinary with 1:3 cement mortar | m2 | 53.7 |  | 0
PAINTING
High Gloss
Timber Surfaces
External quality weather guard paint, two coats, to the following timber surfaces; include surface preparation and undercoat
M.W.24 | Upper surfaces of fascia board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 8.7 |  | 0
Masonry
External quality weather guard paint two coats, to the following smooth concrete surfaces; include surface preparation as specified
M.W.25 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 50.9 |  | 0
|  |  |  | Carried to Collection | 0
Emulsion Paint
Masonry
Internal quality vinyl silk paint, two coats, to the following smooth concrete surfaces; include surface preparation as specified
M.W.26 | Surfaces of walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 53.7 |  | 0
MISCELLANEOUS WORKS
Roofing
M.W.27 | Construct roofing, complete as in the drawings and as specified; include tie beams, purlins, rafters, struts, wall plate, fascia board and all roofing timber, gauge 28 prepainted GCI sheeting and ridges, and 112mm uPVC rain water guttering and DN 80 drainage pipes to the Engineer's satisfaction. | m2 | 34 |  | 0
M.W.28 | Construct 100mm solid reinforced concrete (25) slab complete as in the drawings to the Engineer's satisfaction. | m2 | 10.2144 |  | 0
M.W.29 | Supply and install expanded metal and plastered ceiling nailed to brandering made from sawn treated Cyprus or other similar grade and approved timber in roof structure; complete including 3 coats of matt emulsion paint and 600x600mm hardwood access trap door | m² | 36.3 |  | 0
|  |  |  | Carried to Collection | 0
Windows
Supply and fix the following mild steel casement windows to the Engineers' details constructed from standard steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, plugging and fixing to head jamb and cill
M.W.30 | Mild steel window overall size 1000 x 1100mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 1 |  | 0
M.W.31 | Mild steel window overall size 600 x 600mm high complete with 4mm thick clear glass panes, and burglar proofing | nr | 1 |  | 0
Doors
Supply and fix the following mild steel doors to the Engineers' details constructed from 75 x 50 x 2mm hollow steel sections primed with red oxide paint, painted with three coats of high gloss paint; complete with all necessary iron mongery, 3-lever Yale locking arrangements, and accessories
M.W.32 | Single leaf solid steel door, size 900 x 2100mm; complete | nr | 1 |  | 0
Supply and fix approved solid hardwood with three coats of polyurethane varnish on general surfaces of door as described; 50mm two panel framed door comprising 50 x 100mm stiles, top, middle and bottom rails all grooved and with both panels filled with 30 x 100mm vertical tongued and grooved battens with rubber door stops, all iron mongery and locking arrangements of the following sizes
M.W.33 | 800mm x 2100mm (W x H) | nr | 2 |  | 0
Building Finishes
M.W.34 | Building finishes including, constructing 20x100mm high 1:3 cement-sand skirting, C20 concrete window cills, 700mm wide C20 concrete splash apron, complete to the specifications and as directed by the Engineer | sum | 1 |  | 0
Plumbing and Drainage
M.W.35 | Supply and erect a 250 litre (0.25m3) Polyethylene tank as Polytank, elevated on top of the slab roof at 2.7 m above ground level with galvanised mild steel 80mm steel sectional painted access ladder, with all water supply pipe work and HDPE/GI/PPR fittings, gate valves, ball float valve to OD32mm PN16 and pipework connection to toilet water system complete | Sum | 1 |  | 0
M.W.36 | Allow for supply and installation of standard hand washing basin and standing pedestal(including chieseling, pipework and connections to the soak pit) | nr | 2 |  | 0
M.W.37 | Supply materials and install water supply service pipe work from distribution main to overhead tank, include all HDPE/GI/PPR fittings, saddles, gate valves, adaptors, all accessories, all to PN 16; include processing water connection account with relevant water authority | Sum | 1 |  | 0
0
M.W.38 | Supply and install sanitary appliances for 1no water borne closet toilets (1no. squat type); drainage and plumbing pipework complete as in; Vitreous UK White glazed WC suite P trap pan, 10 litres vitreous UK water cistern with cover, plastic flushing pipe, Vitreous UK white glazed wash hand basins (1no.) with 1 no. 13mm diameter chromium plated pillar tap, 40mm waste outlet grating, plastic plug and chain stay, plastic bottle trap, concealed cast iron fixing brackets; toilet paper holder; DN 15/20 complete water supply pipework and fittings; OD 110 PVC drain pipe work to septic tank, 2 no. brickwork drainage manholes, all to the Engineer's satisfaction | Sum | 1 |  | 0
M.W.39 | Excavate and construct septic tank of effective capacity 1.4m3 (2250x0.675x900mm) in blockwork and reinforced concrete, rendered smooth inside complete with inlet and outlet manholes benching, heavy duty concrete manhole covers, OD 110 PVC ventilation pipe work with fly screen covers complete and clipped to toilet wall, all to the Engineer's satisfaction | Sum | 1 |  | 0
0
M.W.40 | Excavate and construct 1500mm top/bottom diameter x 1.2m deep soak pit including filling with hardcore, covering with 2 layers of gauge 1000 polyethylene sheet complete including connecting to wash hand basins with OD 50mm PVC drain pipes | Sum | 1 |  | 0
Water Supply at the pump house
M.W.41 | Supply all materials and install water supply service pipe from the overhead tank at guard house to the chemical/ pump house, include all HDPE/GI/PPR fittings, gate valves, adaptors, all accessories, all pipes and fittings to OD25mm PN10 | Sum | 1
M.W.42 | Supply all materials and construct a yad tap at the chemical/guard house, 0.6m above ground ground level. All pipes and fittings (to include 1no. gate valve, union, sockets, nipples and long 90 deg. bends etc) to OD15mm (1/2") PN10 | Sum | 1
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page M.W/1 |  |  |  | 0
| Collection, Page M.W/2 |  |  |  | 0
| Collection, Page M.W/3 |  |  |  | 0
| Collection, Page M.W/4 |  |  |  | 0
| Collection, Page M.W/5 |  |  |  | 0
|  |  |  | Carried to Summary | 0

## M-W-11 T&E
GOAL UGANDA
CONSTRUCTION OF MUWAYO TOWN COUNCIL PIPED WATER SUPPLY SYSTEM IN BUGIRI DISTRICT
BILL No. | B-Z- W-11
DESCRIPTION: | TOOLS AND EQUIPMENT
ITEM NO. | ITEM DESCRIPTION | UNIT | QTY | RATE (Ushs) | AMOUNT (Ushs)
PLUMBING TOOLS AND EQUIPMENT
B-Z-11.1 | Blowlamp: pump action, pressure type, approx. 0.5 litre capacity, complete with wind proof nozzle and one set of replacement parts | No. | 1
B-Z-11.2 | Brushes, wire type for cleaning parts, 300 mm long, 3 rows of approximately15 tufts with 25 mm long steel bristles | No. | 1
B-Z-11.3 | File, flat machinist's, length 250 mm, second cut | No. | 1
B-Z-11.4 | File, flat machinist's, length 250 mm, smooth cut | No. | 1
B-Z-11.5 | File, flat machinist's, length 250 mm, bastard cut | No. | 1
B-Z-11.6 | File, half-round machinist's, length 250 mm, smooth cut | No. | 1
B-Z-11.7 | File, half-round machinist's, length 250 mm, but bastard cut | No. | 1
B-Z-11.8 | File handles, 100 x 27 mm | No. | 1
B-Z-11.9 | Hammer, mechanic's, 200 & tempered forged steel head, ash or white hickory handle, polished face | No. | 1
B-Z-11.10 | Precision Level, plumb and spirit, approximately 600 x 25 x 75 mm, varnished beech wood or aluminium, class of accuracy 0.025 mm/m | No. | 1
B-Z-11.11 | Mattocks | No. | 1
B-Z-11.12 | Pliers, arc joint, minimum 5 adjustments, 240 mm long | No. | 1
B-Z-11.13 | Saw, Plumbers, 400 mm, fine tooth edge for cutting metal and coarse teeth for cutting wood, complete with 5No. blades | No. | 1
B-Z-11.14 | Screw drivers, assorted, hammer-proof, non-inflammable plastic handle | Set | 1
B-Z-11.15 | Shovels | No. | 1
B-Z-11.16 | Tape measure, Stanley type steel, metric units, 5 m | No. | 1
B-Z-11.17 | Tapping machine, furnished with ratchet crank for manual operation, for making tappings from DN 15 (1/2") to DN 50 (2") on mains of DN 25 (1”) to DN 300 (12”) | No. | 1
B-Z-11.18 | Die set with stock, for threading from DN 15 to DN 100 | No. | 1
B-Z-11.19 | Vice with parallel jaw 100 mm as Peddinghaus, Matador 10203, portable type, with tripod stand | No. | 1
B-Z-11.20 | Portable disc Makita cutter 750W electric motor driven for disc diameter of approximate 20 cm, including all accessories in steel box, 20No. spare discs shall be provided for steel and 20No. suitable for concrete/stone cutting. | No. | 1
WATER QUALITY TESTING KIT
B-Z-11.21 | Supply and install a floatable chlorine dispenser at the reservoir with chemical cubes for dosage during testing period | No. | 1
B-Z-11.22 | Portable analysis kit such as Potalab 1 (Wag-WE10010) of M/s Wagtech International or similar with reagents to carry out 300 tests for microbiological and physico-chemical testing | Set | 1
MISCELLANEOUS TOOLS
B-Z-11.23 | Contractor's pick axe with point and chisel steel end, length 800 mm | No. | 1
B-Z-11.24 | Steel hoe, blade width 200mm, 1.5kg complete with good wooden handle | No. | 1
B-Z-11.25 | Seamless pressed tray wheelbarrow, steel frame, with pneumatic wheels, 80 litres | No. | 1
B-Z-11.26 | Steel Slashers | No. | 1
B-Z-11.27 | 33CC 2-Cycle Petrol-Powered engine Straight Shaft Attachment Capable String Lawn Trimmer with 17-inch cutting path (including 10No. replacement trimmer lines) | No. | 1
B-Z-11.28 | Steel rakes | No. | 1
|  |  |  | Carried to Summary | 0