## LOT-1 Solar Water System-Workie
Lot-1 | BOQ Solarization system for Raya Kobo (Workie Water Supply Scheme)
NO. | ITEM DESCRIPTION | QTY | UNIT | RATE | AMOUNT -ETB
PART A: | Main components
1 | Renewable Solar Inverter 3x380-480V IP66 22kW, Input Current: 46A. DC-AC inverter with Build-in MPPT (Maximum power point tracking). Frequency 50/60Hz, DC 400-800V | 1 | pc
2 | Min. 575 Watt Mono crystalline solar modules. The price shall include PV combiner 1000VDC box. Note: Total Solar power required is 30KW and minimum number of string is 4. | 52 | Pcs
PART B: | Accessories & Power supply cables
3 | AC circuit breaker compatible with pump and inverter. Each string has its own breaker (OTDCP16, 16A) | 4 | Pcs
4 | 3*16 mm Cable | 45 | M
5 | PV Disconnection Circuit Breaker, with minimum of 25Amp box appropriate for the number of modules and maximum voltage and current of the PV array. The PV breaker shall be supplied and installed for each string. | 4 | pc
6 | 6mm2 single core cable for DC Extension line from PV module | 60 | M
7 | Surge Protection device compatible with controller and pump motor OVR PV40-1000 | 1 | pc
8 | Lightning surge arrestor with copper strips of not less than 25mmx4mm supported by 2" GI pipe with minimum of 3m. | 1 | pc
9 | 5/8 100% copper earth rod with Clamp | 1 | pc
10 | 10mm2 Copper earth cable | 10 | M
11 | Change Over switch compatiuble with the inverter | 1 | Pcs
PART C: | Fire Fighting & Electrical Board
12 | 6 Kg Fire Extinguisher with minimum of 3 years expire date. The price includes red cabine box | 1 | Pcs
13 | Supply and install water proof & secured switch board IP65 that can accommodate the inverter, breaker, surge protector and PV breaker. | 1 | pc
PART D: | Module support structure
Each Footing shall be spaced at 2m center to center in the string
14 | Implementation of (0.4x0.4x0.7)m reinforced concrete type C25 for all mounting foundations and all necessary related work as detailed in the shop drawings. This item includes all excavations, backfill around the footing and formwork. | 1 | LS
15 | Supply and erect a panel support structure made of 2'' Pipe poles welded with Ø10 bar for anchor at one end, 1 1/2" rafters bolted by U-bolt on to 2'' poles end plate, 40x40x3mm C-channel strut will be tied into rafter by U-bolt, the strut has 120 tilt and, the shorter pole shall be minimum of 0.8m above ground level to support the quantity of panels above. | 1 | LS
PART E: | Fencing Works and Commissioning
16 | Fencing around the PV compound with 60x60x3mm angle GS Pipe pole stand to the height of 2.4m above ground level with 1m- 0.8m deep and 450 bend at top 40cm, and erecting using boulder-cement concrete C-20 concerete mix (40cm dia)concrete foundation and bracing diagonals at the corner. The fence shall be constructed from mesh wire(Gabion) of thickness 3 mm and mesh size – 50X50mm each, firmly fixed to the angle iron poles with fence ties.The top 40cm shall be fenced with barbed wire in two strips. The fence should have minimum of 2m distance from the PV Array. Supply and install sheet metal gate door (3mm thick) framed LTZ with size of 200x90cm. Price include painting of anti-rust paint to the angle iron and weld metal bar to anchor the post. NB;-The quality of all matreials should be approved by the Engineer | 1 | LS
17 | Transportation, Installation, Testing & commissioning including testing to determine the actual flowrate delivered by the system once the panels are installed for atleast three hours. Based on the confirmation of pump performance during commissioning procedure. | 1 | LS
SUB TOTAL
VAT-15%
TOTAL Summary