## LOT 1 BOQ Somali-Farda WSS
LOT 1 BOQ Rehabilitation of Solar Water System |  | Somali: Kebribayah woreda Farda WSS (9.2 KW Pump and 11 KW Inverter)
NO. | ITEM DESCRIPTION | QTY | UNIT | RATE | AMOUNT -ETB
PART A: | Main components
1 | Renewable Solar Hybrid Controller DC-AC, RSI 3x208-240V IP66 11kW 48A AC inverter with Build-in MPPT (Maximum power point tracking) | 1 | pc
2 | Mono/poly crystalline solar modules with Min. Power of 615W. The price shall include PV combiner 1000VDC box and other accessories | 21 | pc
3 | Supply and install 9.2 KW Solar Pump with all accessories (including power cables (3*25 mm2), voulcanization) and dry run sensor (with 2*1.5 mm2 cable) with Class C 3" Raiser Pipe and Heavy Duty Socket enough for the number of raiser pipes and 2 pcs 3" GI pipe clamps, 3" check valve, and 3" water Meter. Pump Position is 172 Meters. | 1 | Pcs
PART B: | Power supply cables
4 | 6mm2 single core cable for DC line | 100 | M
5 | 3 X 25 mm2 PVC/SWA 99% copper armoured cable from controller to changeover switch | 20 | M
PART C: | DC accessories and earth protection
6 | PV Disconnection Circuit Breaker, with minimum of 16Amp box appropriate for the number of modules and maximum voltage and current of the PV array. The PV breaker shall be supplied and installed for each string. | 3 | pc
7 | Surge Protection device compatible with controller and pump motor OVR PV40-1000 | 1 | pc
8 | Lightning surge arrestor with copper strips of not less than 25mmx4mm | 1 | pc
9 | 5/8 100% copper earth rod. | 1 | pc
10 | 10mm2 Copper earth cable | 10 | M
PART D: | Controls and Accessories for hybrid operation
11 | Supply and install 100A Change over switch | 1 | pc
12 | Supply and install water proof & secured switch board IP65 that can accommodate the inverter, breaker, surge protector and PV breaker. | 1 | pc
PART E: | Module support structure
Each Footing shall be spaced at 2.5m center to center in the string
13 | Implementation of (0.35x0.35x0.7)m reinforced concrete type C25 for all mounting foundations and all necessary related work as detailed in the shop drawings. This item includes all excavations, backfill around the footing and formwork. | 1 | LS
14 | Supply and erect a panel support structure made of 2'' Pipe poles welded with Ø10 bar for anchor at one end and weld 100x200x3mm plate at the other end, 1 1/2" rafters bolted by U-bolt on to 2'' poles end plate, 60x50x3mm C-channel strut will be tied into rafter by U-bolt, the strut has 90 tilt and, lower end to be minimum 0.7m above ground level to support the quantity of panels above. | 1 | LS
15 | Transportation, installation, testing & commissioning: including testing to determine the actual flowrate delivered by the system once the panels are installed for atleast three hours. Based on the confirmation of pump performance during commissioning procedure. | 1 | LS
PART F: | Fencing Works
16 | Fencing With 2mm Hexagonal wire mesh around the compound with Angle Iron stand to the height of 2m above ground level with 0.6m deep concrete foundation. The fence shall be constructed with 200cm Hexagonal wire mesh and 40*40*1.5mm Angle Iron tied every 0.2mm. The price shall include | 1 | LS
17 | Metal door 90x210cm made from metal LTZ frames with 4mm thick metal sheet. All works should be cut and assembeled to size and shapes of the door schedule upon submittng workshop drawing by the contractor. Unit price includes cylinder lock or similar door stoppers and other necessary accessories for completing the work. | 1 | No
| Total |  |  |  | 0
| VAT 15% |  |  |  | 0
| Grand Total |  |  |  | 0