## Appendix 3.2_LOT2
BoQ for Health Facility Restoration Activity(Health Facility Solarization)
Activity Description and Location |  | LOT 2 Supplying and installation of solar power systems with all necessary materials and fencing, Finto Health Center, Awra Woreda, Afar Region
Donor |  | BHA
Cost Center |  | BSG
Account Code |  | 4049EETG
Technical Specification for 6KW Solar Power System for Health Facilities
S/N | Item Description with standards and recommendations | Unit of Measurement | Quantity | Unit Price | Total Price
SOLAR PANAL, CONTROLLER AND ACCESSORIES
1 | Supplying of SPV module: M. Cell capacity 615Wp,(Optional) Multi/Mono crystalline silicon cell, terrestrial modules design qualification. [About 550Wp cell size for 6.0kwp, 48Vpdc.system voltage with a reliable system design, also applicable]. IEC 61215, IEC 61646 standards, and type-approved/certified multi/mono crystalline silicon cells. | Pcs | 12 |  | 0
2 | Supply SPV Inverter 6 Kw, with charge controller | Pcs | 1 |  | 0
3 | Cable 3*25mm2 | m | 30 |  | 0
4 | Cable 1*4mm2 | m | 30 |  | 0
0
| BATTERY AND ELECTRICAL ACCESSORIES |  |  |  | 0
5 | Battery 200ah,12v Lithium-ion battery Maximum allowable DOD in service shall be 80% with PV Battery Box (Housing/Enclosure)- with an RHS metal structure, well-ventilated, and featuring a lockable door. Including all necessary accessories. | pcs | 20 |  | 0
6 | Combiner Box | pcs | 1 |  | 0
7 | Surge protection device with Controller,lightening surge arrestor with copper string | Set | 1 |  | 0
8 | 100% Copper Earth rod | Pcs | 1 |  | 0
9 | 10mm2 Copper Earth Cable | m | 10 |  | 0
10 | 32Ampere AC Breaker | Pcs | 5 |  | 0
11 | 25Ampere AC Breaker | pcs | 4 |  | 0
12 | 16Ampere AC Breaker | Pcs | 3 |  | 0
13 | 10Ampere AC Breaker | pcs | 3 |  | 0
0
STRUCTURE,TRANSPORT SERVICE AND INSTALLATION
14 | PV Mounting Structure: Supply and erect a panel support structure made of 2'' Pipe poles welded with Ø10 bar for anchor at one end and weld 100x200x4mm plate at the other end with four holes at the corner, 1 1/2" rafters bolted by U-bolt on to 2'' poles end plate, 40x40x4mm C-channel strut will be tied into rafter by U-bolt, the strut has 130 tilt and lower end to be minimum 1 m above ground level to support the quantity of panels above. All joints to be bolt and nuts with spot welding | Set | 1 |  | 0
15 | Controller and DC breaker locker made of metal frame | ls | 1 |  | 0
16 | Installation, Testing, Transportation and all Solar system with checking all lighting and Cooling system in all room of health center | ls | 1 |  | 0
0
FENCE WORK MATERIALS
17 | Fencing around the PV compound (10m*10m) with 60x60x3mm angle GS Pipe pole stand to the height of 2.4m above ground level with 1m- 0.8m deep and 450 bend at top 40cm, and erecting using boulder-cement concrete C-20 concerete mix (40cm dia)concrete foundation and bracing diagonals at the corner. The fence shall be constructed from mesh wire(Gabion) of thickness 2 mm mesh size – 50X50mm each, firmly fixed to the angle iron poles with fence ties.The top 40cm shall be fenced with barbed wire in two strips. Price include painting of anti-rust paint to the angle iron and weld metal bar to anchor the post. NB;-The quality of all matreials should be approved by the Engineer | ls | 1 |  | 0
18 | Supply and install sheet metal gate door (3mm thick) framed LTZ with size of 200x90cm. | pc | 1 |  | 0
Sub Total |  |  |  |  | 0
Total |  |  |  |  | 0
VAT 15% |  |  |  |  | 0
Grand Total |  |  |  |  | 0