## BoQ HF solarization (2)
Technical Specification for 3KW Solar Power System for Health Facilities
S/N | Item Description with standards and recommendations | Unit of Measurement | Quantity | Unit Price | Total Price
SOLAR PANAL, CONTROLLER AND ACCESSORIES
1 | Supplying of SPV module: M. Cell capacity 615Wp,(Optional) Multi/Mono crystalline silicon cell, terrestrial modules design qualification. IEC 61215, IEC 61646 standards, and type-approved/certified multi/mono crystalline silicon cells. | Pcs | 6
2 | Supply SPV Inverter 3KW, with charge controller | Pcs | 1
3 | Cable 3*25mm2 | m | 30
4 | Cable 1*4mm2 | m | 50
0
| BATTERY AND ELECTRICAL ACCESSORIES |  |  |  | 0
5 | Battery 200Ah ,12v or equivalent battery storage of 14.4kWh with BMS | pcs | 6
6 | Combiner Box | pcs | 1
7 | Surge protection device with Controller,lightening surge arrestor with copper string | Set | 1
8 | 100% Copper Earth rod | Pcs | 1
9 | 10mm2 Copper Earth Cable | m | 10
10 | 32Ampere AC Breaker | Pcs | 5
11 | 25Ampere AC Breaker | pcs | 4
12 | 16Ampere AC Breaker | Pcs | 3
13 | 10Ampere AC Breaker | pcs | 3
0
STRUCTURE,TRANSPORT SERVICE AND INSTALLATION
14 | Each Footing spacing shall not exceed 2 m c/c along the length and width.
14.1 | Implementation of (0.35x0.35x0.6)m reinforced concrete type C25 for all mounting foundations and all necessary related work as detailed in the shop drawings. This item includes all excavations, backfill around the footing and formwork. | LS | 1
14.2 | Supply and erect a panel support structure made of 2'' Pipe poles welded with Ø10 bar for anchor at one end and weld 200x200x4mm plate at the other end with four holes at the corner, 1 1/2" rafters bolted by U-bolt on to 2'' poles end plate, 60x30x4mm C-channel strut will be tied into rafter by U-bolt, the strut has 50 tilt and lower end to be minimum 1.5m above ground level to support the quantity of panels above. All joints to be bolt and nuts with spot welding | LS | 1
15 | Controller and DC breaker locker made of metal frame | ls | 1
16 | Installation, Testing, Transportation and all Solar system with checking all lighting and Cooling system in all room of health center | ls | 1
FENCE WORK MATERIALS
17 | Perimeter Fencing around the Solar Array: Supply and install 40 × 40 × 3 mm angle iron posts with 2 mm thick wire mesh around solar panel (2 meter away in each side). Posts shall be spaced at 1.5 m c/c, each 2.5 m long, with 2.0 m above NGL and 0.5 m below ground, and embedded in a concrete base to a depth of 0.5 m. Measurement shall be taken horizontally along the fence line. The item shall include a 0.90 m × 2.10 m fabricated metal sheet gate of 4 mm thickness, complete with hinges, latch, and lock, as well as a 20 cm thick grade beam projecting 20 cm above NGL. The bottom edge of the wire mesh shall be anchored to the grade beam along the full perimeter. | ls | 1
Sub Total |  |  |  |  | 0
Total |  |  |  |  | 0
VAT 15% |  |  |  |  | 0
Total for One HC |  |  |  |  | 0